## Base Case Description
Base Case Description
Open Switches | Generator Setpoints | kW | Solar irradiation | Sample Points for validation
[5 empty] | Node | Line | Feeder
Line.WD701_48332_sw | SteamGen1 | 1000 | 100% of possible | #1 | E192860 | Line.ln5815900-1 | S1
Line.WF586_48332_sw | MicroTurb-1 | 50 | All PV at rated MPP output | #2 | M1047303 | Line.ln6380847-1 | S2
Line.WF856_48332_sw | MicroTurb-2 | 0 |  | #3 | E203026 | Line.ln6044631-1 | S3
Line.WG127_48332_sw | MicroTurb-3 | 0 |  | #4 | L2955077 | Line.ln6381853-1 | S1
LINE.LN0653457_SW | MicroTurb-4 | 100 |  | #5 | M1069310 | Line.ln5486729-1 | S2
LINE.V7173_48332_SW | Diesel620 | 0 |  | #6 | M1026907 | Line.ln6350537-1 | S3
LINE.TSW803273_SW | Diesel590 | 0
LINE.A333_48332_SW | LNGEngine100 | 0
LINE.TSW320328_SW | LNGEngine1800 | 0
LINE.A8645_48332_SW
LINE.TSW568613_SW
1
2
3
4
5
6

## Node voltages
Node | VA (volts) | VB (volts) | VC (volts) | VA (pu) | VB (pu) | VC (pu) | Feeder | Comments
E192860 | 7376.04 | 7371.13 | 7368.99 | 1.0245 | 1.0238 | 1.0235 | S1 | *Also used for original 8500 node model validation by RC Dugan
M1047303 | 7380.88 | 7365.7 | 7326.41 | 1.0252 | 1.0231 | 1.0176 | S2 | *Also used for original 8500 node model validation by RC Dugan
E203026 | 7374.68 | 7389.26 | 7388.14 | 1.0243 | 1.0263 | 1.0262 | S3
L2955077 | 7316.47 | 7324.12 | 7343.11 | 1.0162 | 1.0173 | 1.0199 | S1 | *Also used for original 8500 node model validation by RC Dugan
M1069310 | 7413.4 | 7197.58 | 7189.33 | 1.0297 | 0.99973 | 0.99858 | S2
M1026907 | 7010.92 | 7273.69 | 7336.17 | 0.9738 | 1.0103 | 1.019 | S3 | *Also used for original 8500 node model validation by RC Dugan

## Line Flows
Element | Phase | kW | kVAr | Amperes | Feeder | Comment
Line.ln5815900-1 | A | 971.845 | -16.9369 | 131.777 | S1 | *Also used for original 8500 node model validation by RC Dugan
| B | 941.489 | -29.0441 | 127.787
| C | 1078.05 | 13.2183 | 146.306
| Total | 2991.384 | -32.7627
Line.ln6380847-1 | A | 587.994 | 152.484 | 82.2877 | S2 | *Also used for original 8500 node model validation by RC Dugan
| B | 818.5 | 88.1571 | 111.811
| C | 1055.74 | 34.6632 | 144.228
| Total | 2462.234 | 275.3043
Line.ln6044631-1 | A | 1261.92 | 451.784 | 182.308 | S3
| B | 1173.37 | 426.611 | 169.162
| C | 599.013 | 225.402 | 86.6327
| Total | 3034.303 | 1103.797
Line.ln6381853-1 | A | 566.676 | 171.075 | 80.883 | S1 | *Also used for original 8500 node model validation by RC Dugan
| B | 624.265 | 177.319 | 88.5847
| C | 526.74 | 156.395 | 74.8184
| Total | 1717.681 | 504.789
Line.ln5486729-1 | A | 146.896 | 41.9015 | 20.6053 | S2
| B | 399.62 | 112.048 | 57.6627
| C | 331.087 | 98.5565 | 48.0496
| Total | 877.603 | 252.506
Line.ln6350537-1 | A | 212.012 | 56.6074 | 31.2868 | S3 | *Also used for original 8500 node model validation by RC Dugan
| B | 196.081 | 51.9347 | 27.8795
| C | 164.93 | 43.8034 | 23.2561
| Total | 573.023 | 152.3455

## Tap Positions
Name | Tap | Min | Max | Step | Position
feeder_reg1a | 0.98125 | 0.9 | 1.1 | 0.00625 | -3
feeder_reg1b | 0.98125 | 0.9 | 1.1 | 0.00625 | -3
feeder_reg1c | 0.98125 | 0.9 | 1.1 | 0.00625 | -3
feeder_reg2a | 0.9875 | 0.9 | 1.1 | 0.00625 | -2
feeder_reg2b | 0.9875 | 0.9 | 1.1 | 0.00625 | -2
feeder_reg2c | 0.98125 | 0.9 | 1.1 | 0.00625 | -3
feeder_reg3a | 0.99375 | 0.9 | 1.1 | 0.00625 | -1
feeder_reg3b | 0.99375 | 0.9 | 1.1 | 0.00625 | -1
feeder_reg3c | 0.9875 | 0.9 | 1.1 | 0.00625 | -2
vreg2_a | 0.95625 | 0.9 | 1.1 | 0.00625 | -7
vreg2_b | 0.975 | 0.9 | 1.1 | 0.00625 | -4
vreg2_c | 0.99375 | 0.9 | 1.1 | 0.00625 | -1
vreg3_a | 1.0312 | 0.9 | 1.1 | 0.00625 | 5
vreg3_b | 1.025 | 0.9 | 1.1 | 0.00625 | 4
vreg3_c | 1.025 | 0.9 | 1.1 | 0.00625 | 4
vreg4_a | 0.99375 | 0.9 | 1.1 | 0.00625 | -1
vreg4_b | 0.975 | 0.9 | 1.1 | 0.00625 | -4
vreg4_c | 0.96875 | 0.9 | 1.1 | 0.00625 | -5