## 240busWECC_2018_PSS
0 | 100 | 34 |  |  | / WECC 240 SYSTEM | V0.2 | DEVELOPED BY NREL. CONTACT: HAOYU.YUAN@NREL.GOV
This is a reduced WECC 240-bus power system model reflecting WECC generation resource mix in 2018 and representing the summer peak load. It was developed by NREL and contains no CEII.
Reference: H. Yuan | R. S. Biswas | J. Tan and Y. Zhang | "Developing a Reduced 240-Bus WECC Dynamic Model for Frequency Response Study of High Renewable Integration | IEEE/PES Transmission and Distribution Conference and Exposition (T&D), Chicago, IL, USA, 2020.
0 / END OF SYSTEM-WIDE DATA | BEGIN BUS DATA
1001 | 'FOURCORN ' | 500 | 1 | 1 | 3 | 1 | 1.034 | 5.5785 | 1.1 | 0.9 | 1.1 | 0.9
1002 | 'FOURCORN ' | 345 | 1 | 1 | 3 | 1 | 1.014 | 8.3685 | 1.1 | 0.9 | 1.1 | 0.9
1003 | 'FOURCORN ' | 230 | 1 | 1 | 10 | 1 | 0.97318 | -0.292 | 1.1 | 0.9 | 1.1 | 0.9
1004 | 'SAN JUAN ' | 345 | 1 | 1 | 10 | 1 | 1.03 | 18.8075 | 1.1 | 0.9 | 1.1 | 0.9
1032 | 'FCNGN4CC ' | 20 | 2 | 1 | 10 | 1 | 1.0139 | 8.9503 | 1.1 | 0.9 | 1.1 | 0.9
1034 | 'SJUAN G4 ' | 20 | 2 | 1 | 10 | 1 | 1.0334 | 20.4253 | 1.1 | 0.9 | 1.1 | 0.9
1101 | 'CORONADO ' | 500 | 1 | 1 | 3 | 1 | 1.01 | -13.5878 | 1.1 | 0.9 | 1.1 | 0.9
1102 | 'CHOLLA ' | 345 | 1 | 1 | 3 | 1 | 0.99465 | -4.7874 | 1.1 | 0.9 | 1.1 | 0.9
1131 | 'CORONADO ' | 20 | 2 | 1 | 3 | 1 | 1.0095 | -12.8589 | 1.1 | 0.9 | 1.1 | 0.9
1201 | 'MOENKOPI ' | 500 | 1 | 1 | 3 | 1 | 1.0914 | -6.6183 | 1.1 | 0.9 | 1.1 | 0.9
1202 | 'NAVAJO ' | 500 | 1 | 1 | 3 | 1 | 1.08 | -3.8673 | 1.1 | 0.9 | 1.1 | 0.9
1232 | 'NAVAJO 2 ' | 20 | 2 | 1 | 3 | 1 | 1.0799 | -3.0358 | 1.1 | 0.9 | 1.1 | 0.9
1301 | 'MEAD ' | 500 | 1 | 1 | 3 | 1 | 1.045 | -9.8666 | 1.1 | 0.9 | 1.1 | 0.9
1302 | 'H ALLEN ' | 500 | 1 | 1 | 9 | 1 | 1.0244 | -11.6849 | 1.1 | 0.9 | 1.1 | 0.9
1303 | 'H ALLEN ' | 345 | 1 | 1 | 9 | 1 | 1.005 | -15.2256 | 1.1 | 0.9 | 1.1 | 0.9
1331 | 'HOOVER ' | 20 | 2 | 1 | 3 | 1 | 1.0451 | -8.7861 | 1.1 | 0.9 | 1.1 | 0.9
1333 | 'H ALLEN ' | 20 | 2 | 1 | 9 | 1 | 1.0079 | -13.7701 | 1.1 | 0.9 | 1.1 | 0.9
1401 | 'PALOVRDE ' | 500 | 1 | 1 | 3 | 1 | 1.035 | -14.7822 | 1.1 | 0.9 | 1.1 | 0.9
1402 | 'WESTWING ' | 500 | 1 | 1 | 3 | 1 | 1.059 | -20.357 | 1.1 | 0.9 | 1.1 | 0.9
1403 | 'PARKER ' | 230 | 1 | 1 | 3 | 1 | 1.0353 | -14.4059 | 1.1 | 0.9 | 1.1 | 0.9
1431 | 'PALOVRD2 ' | 20 | 2 | 1 | 3 | 1 | 1.04 | -12.4298 | 1.1 | 0.9 | 1.1 | 0.9
2000 | 'MEXICO ' | 230 | 1 | 4 | 7 | 1 | 1 | -16.7754 | 1.1 | 0.9 | 1.1 | 0.9
2030 | 'MEXICO ' | 20 | 2 | 4 | 7 | 1 | 1.0013 | -16.0721 | 1.1 | 0.9 | 1.1 | 0.9
2100 | 'IMPERIAL ' | 230 | 1 | 2 | 2 | 1 | 1.035 | -12.4531 | 1.1 | 0.9 | 1.1 | 0.9
2130 | 'IMPERIAL ' | 20 | 2 | 2 | 2 | 1 | 1.0355 | -12.0979 | 1.1 | 0.9 | 1.1 | 0.9
2201 | 'MIGUEL ' | 500 | 1 | 2 | 2 | 1 | 0.99375 | -26.5153 | 1.1 | 0.9 | 1.1 | 0.9
2202 | 'MIGUEL ' | 230 | 1 | 2 | 2 | 1 | 0.99067 | -27.7043 | 1.1 | 0.9 | 1.1 | 0.9
2203 | 'MISSION ' | 230 | 1 | 2 | 2 | 1 | 1.005 | -27.9287 | 1.1 | 0.9 | 1.1 | 0.9
2233 | 'MISSION ' | 20 | 2 | 2 | 2 | 1 | 1.0069 | -27.6476 | 1.1 | 0.9 | 1.1 | 0.9
2301 | 'IMPRLVLY ' | 500 | 1 | 2 | 2 | 1 | 1.0356 | -14.9787 | 1.1 | 0.9 | 1.1 | 0.9
2302 | 'IMPRLVLY ' | 230 | 1 | 2 | 2 | 1 | 1.035 | -13.8866 | 1.1 | 0.9 | 1.1 | 0.9
2332 | 'IMPRLVLY ' | 20 | 2 | 2 | 2 | 1 | 1.0352 | -13.6518 | 1.1 | 0.9 | 1.1 | 0.9
2400 | 'DEVERS ' | 500 | 1 | 2 | 2 | 1 | 1.0295 | -19.7851 | 1.1 | 0.9 | 1.1 | 0.9
2401 | 'LUGO ' | 500 | 1 | 2 | 2 | 1 | 1.05 | -13.6953 | 1.1 | 0.9 | 1.1 | 0.9
2402 | 'MIRALOMA ' | 500 | 1 | 2 | 2 | 1 | 1.0317 | -18.0034 | 1.1 | 0.9 | 1.1 | 0.9
2403 | 'VALLEY ' | 500 | 1 | 2 | 2 | 1 | 1.0271 | -22.3928 | 1.1 | 0.9 | 1.1 | 0.9
2404 | 'VINCENT ' | 500 | 1 | 2 | 2 | 1 | 1.0391 | -9.929 | 1.1 | 0.9 | 1.1 | 0.9
2405 | 'SYLMAR S ' | 230 | 1 | 2 | 2 | 1 | 1.0115 | -11.0446 | 1.1 | 0.9 | 1.1 | 0.9
2406 | 'EAGLROCK ' | 230 | 1 | 2 | 2 | 1 | 1.0078 | -14.9652 | 1.1 | 0.9 | 1.1 | 0.9
2407 | 'LITEHIPE ' | 230 | 1 | 2 | 2 | 1 | 0.97489 | -20.8953 | 1.1 | 0.9 | 1.1 | 0.9
2408 | 'MESA CAL ' | 230 | 1 | 2 | 2 | 1 | 1.009 | -9.1772 | 1.1 | 0.9 | 1.1 | 0.9
2409 | 'MIRALOMA ' | 230 | 1 | 2 | 2 | 1 | 1.02 | -18.7773 | 1.1 | 0.9 | 1.1 | 0.9
2410 | 'PARDEE ' | 230 | 1 | 2 | 2 | 1 | 1.0071 | -14.6945 | 1.1 | 0.9 | 1.1 | 0.9
2411 | 'VINCENT ' | 230 | 1 | 2 | 2 | 1 | 1.0203 | -11.4155 | 1.1 | 0.9 | 1.1 | 0.9
2431 | 'LUGO ' | 20 | 2 | 2 | 2 | 1 | 1.05 | -13.6693 | 1.1 | 0.9 | 1.1 | 0.9
2434 | 'VINCENT ' | 20 | 2 | 2 | 2 | 1 | 1.02 | -11.388 | 1.1 | 0.9 | 1.1 | 0.9
2438 | 'MESA CAL ' | 20 | 2 | 2 | 2 | 1 | 1.0098 | -7.7532 | 1.1 | 0.9 | 1.1 | 0.9
2439 | 'MIRALOMA ' | 20 | 2 | 2 | 2 | 1 | 1.0198 | -18.7223 | 1.1 | 0.9 | 1.1 | 0.9
2501 | 'SERRANO ' | 500 | 1 | 2 | 2 | 1 | 1.0269 | -20.2708 | 1.1 | 0.9 | 1.1 | 0.9
2502 | 'SERRANO ' | 230 | 1 | 2 | 2 | 1 | 1.0232 | -21.6056 | 1.1 | 0.9 | 1.1 | 0.9
2503 | 'S.ONOFRE ' | 230 | 1 | 2 | 2 | 1 | 1.009 | -23.5705 | 1.1 | 0.9 | 1.1 | 0.9
2533 | 'S.ONOFRE ' | 20 | 2 | 2 | 2 | 1 | 1.0096 | -23.0364 | 1.1 | 0.9 | 1.1 | 0.9
2600 | 'ADELANTO ' | 500 | 1 | 2 | 2 | 1 | 1.0558 | -9.3695 | 1.1 | 0.9 | 1.1 | 0.9
2601 | 'RINALDI ' | 500 | 1 | 2 | 2 | 1 | 1.0479 | -9.8178 | 1.1 | 0.9 | 1.1 | 0.9
2602 | 'STA E ' | 500 | 1 | 2 | 2 | 1 | 1.0225 | -9.435 | 1.1 | 0.9 | 1.1 | 0.9
2603 | 'VICTORVL ' | 500 | 1 | 2 | 2 | 1 | 1.0566 | -10.0289 | 1.1 | 0.9 | 1.1 | 0.9
2604 | 'INTERMT ' | 345 | 1 | 2 | 2 | 1 | 1.03 | -3.339 | 1.1 | 0.9 | 1.1 | 0.9
2605 | 'STA B1 ' | 287 | 1 | 2 | 2 | 1 | 1.021 | -7.2426 | 1.1 | 0.9 | 1.1 | 0.9
2606 | 'STA B2 ' | 287 | 1 | 2 | 2 | 1 | 1.021 | -7.2426 | 1.1 | 0.9 | 1.1 | 0.9
2607 | 'VICTORVL ' | 287 | 1 | 2 | 2 | 1 | 1.0473 | -9.098 | 1.1 | 0.9 | 1.1 | 0.9
2608 | 'CASTAIC ' | 230 | 1 | 2 | 2 | 1 | 1.015 | -9.4369 | 1.1 | 0.9 | 1.1 | 0.9
2609 | 'GLENDAL ' | 230 | 1 | 2 | 2 | 1 | 0.99971 | -7.7201 | 1.1 | 0.9 | 1.1 | 0.9
2610 | 'HAYNES ' | 230 | 1 | 2 | 2 | 1 | 1.004 | 6.4589 | 1.1 | 0.9 | 1.1 | 0.9
2611 | 'OLIVE ' | 230 | 1 | 2 | 2 | 1 | 1.015 | -9.6301 | 1.1 | 0.9 | 1.1 | 0.9
2612 | 'RINALDI ' | 230 | 1 | 2 | 2 | 1 | 1.0136 | -9.996 | 1.1 | 0.9 | 1.1 | 0.9
2613 | 'RIVER ' | 230 | 1 | 2 | 2 | 1 | 0.99477 | -4.2231 | 1.1 | 0.9 | 1.1 | 0.9
2614 | 'STA BLD ' | 230 | 1 | 2 | 2 | 1 | 1.0022 | -5.8005 | 1.1 | 0.9 | 1.1 | 0.9
2615 | 'STA E ' | 230 | 1 | 2 | 2 | 1 | 1.0054 | -9.1473 | 1.1 | 0.9 | 1.1 | 0.9
2616 | 'STA F ' | 230 | 1 | 2 | 2 | 1 | 0.9967 | -4.5571 | 1.1 | 0.9 | 1.1 | 0.9
2617 | 'STA G ' | 230 | 1 | 2 | 2 | 1 | 0.99769 | -6.2866 | 1.1 | 0.9 | 1.1 | 0.9
2618 | 'STA J ' | 230 | 1 | 2 | 2 | 1 | 1.0111 | -10.9936 | 1.1 | 0.9 | 1.1 | 0.9
2619 | 'SYLMARLA ' | 230 | 1 | 2 | 2 | 1 | 1.0125 | -9.6918 | 1.1 | 0.9 | 1.1 | 0.9
2620 | 'VALLEY ' | 230 | 1 | 2 | 2 | 1 | 1.0093 | -10.0536 | 1.1 | 0.9 | 1.1 | 0.9
2621 | 'STA B ' | 138 | 1 | 2 | 2 | 1 | 1.0128 | -6.9051 | 1.1 | 0.9 | 1.1 | 0.9
2630 | 'HAYNES3G ' | 20 | 2 | 2 | 2 | 1 | 1.0049 | 7.1069 | 1.1 | 0.9 | 1.1 | 0.9
2631 | 'OLIVE ' | 20 | 2 | 2 | 2 | 1 | 1.0152 | -9.5656 | 1.1 | 0.9 | 1.1 | 0.9
2634 | 'INTERM1G ' | 20 | 2 | 2 | 2 | 1 | 1.0299 | -2.924 | 1.1 | 0.9 | 1.1 | 0.9
2637 | 'OWENS G ' | 20 | 2 | 2 | 2 | 1 | 1.0138 | -9.9729 | 1.1 | 0.9 | 1.1 | 0.9
2638 | 'CASTAI4G ' | 20 | 2 | 2 | 2 | 1 | 1.015 | -9.3813 | 1.1 | 0.9 | 1.1 | 0.9
2901 | 'ELDORADO ' | 500 | 1 | 2 | 2 | 1 | 1.1074 | -9.9996 | 1.1 | 0.9 | 1.1 | 0.9
2902 | 'MOHAVE ' | 500 | 1 | 2 | 2 | 1 | 1.1174 | -11.1977 | 1.1 | 0.9 | 1.1 | 0.9
3101 | 'EMBRCDRD ' | 230 | 1 | 2 | 2 | 1 | 0.98132 | -7.7767 | 1.1 | 0.9 | 1.1 | 0.9
3102 | 'MARTIN ' | 230 | 1 | 2 | 2 | 1 | 0.98603 | -6.6336 | 1.1 | 0.9 | 1.1 | 0.9
3103 | 'SANMATEO ' | 230 | 1 | 2 | 2 | 1 | 0.99272 | -4.5012 | 1.1 | 0.9 | 1.1 | 0.9
3104 | 'MARTIN ' | 115 | 1 | 2 | 2 | 1 | 0.98581 | -11.495 | 1.1 | 0.9 | 1.1 | 0.9
3105 | 'POTRERO ' | 115 | 1 | 2 | 2 | 1 | 1 | -11.5056 | 1.1 | 0.9 | 1.1 | 0.9
3133 | 'SANMATEO ' | 20 | 2 | 2 | 2 | 1 | 0.99266 | -4.4922 | 1.1 | 0.9 | 1.1 | 0.9
3135 | 'POTRERO ' | 20 | 2 | 2 | 2 | 1 | 1.0004 | -11.4426 | 1.1 | 0.9 | 1.1 | 0.9
3201 | 'C.COSTA ' | 230 | 1 | 2 | 2 | 1 | 1.0036 | -4.5744 | 1.1 | 0.9 | 1.1 | 0.9
3202 | 'MORAGA ' | 230 | 1 | 2 | 2 | 1 | 1.0023 | -4.1296 | 1.1 | 0.9 | 1.1 | 0.9
3203 | 'NEWARK ' | 230 | 1 | 2 | 2 | 1 | 1.0006 | -4.2221 | 1.1 | 0.9 | 1.1 | 0.9
3204 | 'PITSBURG ' | 230 | 1 | 2 | 2 | 1 | 1.01 | 0.1458 | 1.1 | 0.9 | 1.1 | 0.9
3205 | 'SOBRANTE ' | 230 | 1 | 2 | 2 | 1 | 1.0008 | -2.5203 | 1.1 | 0.9 | 1.1 | 0.9
3234 | 'PITSBURG ' | 20 | 2 | 2 | 2 | 1 | 1.0121 | 1.2652 | 1.1 | 0.9 | 1.1 | 0.9
3301 | 'METCALF ' | 500 | 1 | 2 | 2 | 1 | 1.0113 | -4.7303 | 1.1 | 0.9 | 1.1 | 0.9
3302 | 'JEFFERSN ' | 230 | 1 | 2 | 2 | 1 | 0.9843 | -7.6693 | 1.1 | 0.9 | 1.1 | 0.9
3303 | 'METCALF ' | 230 | 1 | 2 | 2 | 1 | 1 | -5.4781 | 1.1 | 0.9 | 1.1 | 0.9
3304 | 'MONTAVIS ' | 230 | 1 | 2 | 2 | 1 | 0.98986 | -7.0451 | 1.1 | 0.9 | 1.1 | 0.9
3305 | 'RAVENSWD ' | 230 | 1 | 2 | 2 | 1 | 0.99494 | -4.7831 | 1.1 | 0.9 | 1.1 | 0.9
3333 | 'METCALF ' | 20 | 2 | 2 | 2 | 1 | 1.0008 | -5.246 | 1.1 | 0.9 | 1.1 | 0.9
3401 | 'GREGG ' | 230 | 1 | 2 | 2 | 1 | 0.96667 | -13.8507 | 1.1 | 0.9 | 1.1 | 0.9
3402 | 'HELMS PP ' | 230 | 1 | 2 | 2 | 1 | 0.9688 | -13.8643 | 1.1 | 0.9 | 1.1 | 0.9
3403 | 'MC CALL ' | 230 | 1 | 2 | 2 | 1 | 1 | -1.5414 | 1.1 | 0.9 | 1.1 | 0.9
3404 | 'PANOCHE ' | 230 | 1 | 2 | 2 | 1 | 0.98837 | -8.6626 | 1.1 | 0.9 | 1.1 | 0.9
3405 | 'WILSON ' | 230 | 1 | 2 | 2 | 1 | 0.9621 | -15.576 | 1.1 | 0.9 | 1.1 | 0.9
3432 | 'HELMS PP ' | 20 | 1 | 2 | 2 | 1 | 0.9688 | -13.8643 | 1.1 | 0.9 | 1.1 | 0.9
3433 | 'MC CALL ' | 20 | 2 | 2 | 2 | 1 | 1.0002 | -1.1903 | 1.1 | 0.9 | 1.1 | 0.9
3501 | 'FULTON ' | 230 | 1 | 2 | 2 | 1 | 1 | 1.6159 | 1.1 | 0.9 | 1.1 | 0.9
3531 | 'FULTON ' | 20 | 2 | 2 | 2 | 1 | 1.0004 | 1.9278 | 1.1 | 0.9 | 1.1 | 0.9
3601 | 'HUMBOLDT ' | 115 | 1 | 2 | 2 | 1 | 1.015 | -3.945 | 1.1 | 0.9 | 1.1 | 0.9
3631 | 'HUMBOLDT ' | 20 | 2 | 2 | 2 | 1 | 1.0148 | -3.918 | 1.1 | 0.9 | 1.1 | 0.9
3701 | 'SUMMIT ' | 115 | 1 | 1 | 9 | 1 | 1.0066 | -20.6887 | 1.1 | 0.9 | 1.1 | 0.9
3731 | 'SUMMIT ' | 20 | 2 | 1 | 9 | 1 | 1.006 | -20.6259 | 1.1 | 0.9 | 1.1 | 0.9
3801 | 'DIABLO ' | 500 | 1 | 2 | 2 | 1 | 1.049 | 0.2332 | 1.1 | 0.9 | 1.1 | 0.9
3802 | 'GATES ' | 500 | 1 | 2 | 2 | 1 | 1.0371 | -5.7476 | 1.1 | 0.9 | 1.1 | 0.9
3803 | 'MIDWAY ' | 500 | 1 | 2 | 2 | 1 | 1.0462 | -7.1165 | 1.1 | 0.9 | 1.1 | 0.9
3804 | 'GATES ' | 230 | 1 | 2 | 2 | 1 | 1.0023 | -7.1239 | 1.1 | 0.9 | 1.1 | 0.9
3805 | 'MIDWAY ' | 230 | 1 | 2 | 2 | 1 | 1.035 | -6.6568 | 1.1 | 0.9 | 1.1 | 0.9
3806 | 'MORROBAY ' | 230 | 1 | 2 | 2 | 1 | 1.019 | -3.5261 | 1.1 | 0.9 | 1.1 | 0.9
3831 | 'DIABLO1 ' | 20 | 2 | 2 | 2 | 1 | 1.0488 | 0.7821 | 1.1 | 0.9 | 1.1 | 0.9
3835 | 'MIDWAY ' | 20 | 2 | 2 | 2 | 1 | 1.0353 | -6.5555 | 1.1 | 0.9 | 1.1 | 0.9
3836 | 'MORROBAY ' | 20 | 2 | 2 | 2 | 1 | 1.019 | -3.3388 | 1.1 | 0.9 | 1.1 | 0.9
3891 | 'GATES1 ' | 500 | 1 | 2 | 2 | 1 | 1.0522 | -9.2502 | 1.1 | 0.9 | 1.1 | 0.9
3892 | 'MIDWAY1 ' | 500 | 1 | 2 | 2 | 1 | 1.0387 | -3.908 | 1.1 | 0.9 | 1.1 | 0.9
3893 | 'MIDWAY2 ' | 500 | 1 | 2 | 2 | 1 | 1.0335 | -13.1513 | 1.1 | 0.9 | 1.1 | 0.9
3894 | 'MIDWAY3 ' | 500 | 1 | 2 | 2 | 1 | 1.0385 | -3.8546 | 1.1 | 0.9 | 1.1 | 0.9
3895 | 'MIDWAY4 ' | 500 | 1 | 2 | 2 | 1 | 1.0337 | -13.1723 | 1.1 | 0.9 | 1.1 | 0.9
3896 | 'MIDWAY5 ' | 500 | 1 | 2 | 2 | 1 | 1.0389 | -3.6959 | 1.1 | 0.9 | 1.1 | 0.9
3897 | 'MIDWAY6 ' | 500 | 1 | 2 | 2 | 1 | 1.0356 | -13.0099 | 1.1 | 0.9 | 1.1 | 0.9
3901 | 'LOSBANOS ' | 500 | 1 | 2 | 2 | 1 | 1.0299 | -6.014 | 1.1 | 0.9 | 1.1 | 0.9
3902 | 'MOSSLAND ' | 500 | 1 | 2 | 2 | 1 | 1 | -2.2632 | 1.1 | 0.9 | 1.1 | 0.9
3903 | 'TESLA ' | 500 | 1 | 2 | 2 | 1 | 1.0347 | -5.2887 | 1.1 | 0.9 | 1.1 | 0.9
3904 | 'VACA-DIX ' | 500 | 1 | 2 | 2 | 1 | 1.0341 | -5.4622 | 1.1 | 0.9 | 1.1 | 0.9
3905 | 'TABLE MT ' | 500 | 1 | 2 | 2 | 1 | 1.0492 | -6.1484 | 1.1 | 0.9 | 1.1 | 0.9
3906 | 'ROUND MT ' | 500 | 1 | 2 | 2 | 1 | 1.0699 | -5.5014 | 1.1 | 0.9 | 1.1 | 0.9
3907 | 'BELLOTA ' | 230 | 1 | 2 | 2 | 1 | 0.96956 | -13.7171 | 1.1 | 0.9 | 1.1 | 0.9
3908 | 'BRIGHTON ' | 230 | 1 | 2 | 2 | 1 | 0.97516 | -16.5874 | 1.1 | 0.9 | 1.1 | 0.9
3909 | 'COLGATE ' | 230 | 1 | 2 | 2 | 1 | 0.98747 | -17.7611 | 1.1 | 0.9 | 1.1 | 0.9
3910 | 'CORTINA ' | 230 | 1 | 2 | 2 | 1 | 0.97959 | -12.9925 | 1.1 | 0.9 | 1.1 | 0.9
3911 | 'COTWDPGE ' | 230 | 1 | 2 | 2 | 1 | 1.043 | -4.1388 | 1.1 | 0.9 | 1.1 | 0.9
3912 | 'GLENN ' | 230 | 1 | 2 | 2 | 1 | 1.0245 | -10.2031 | 1.1 | 0.9 | 1.1 | 0.9
3913 | 'GOLDHILL ' | 230 | 1 | 2 | 2 | 1 | 0.98796 | -12.6866 | 1.1 | 0.9 | 1.1 | 0.9
3914 | 'IGNACIO ' | 230 | 1 | 2 | 2 | 1 | 0.99136 | -2.1378 | 1.1 | 0.9 | 1.1 | 0.9
3915 | 'LAKEVILE ' | 230 | 1 | 2 | 2 | 1 | 0.99702 | -3.3855 | 1.1 | 0.9 | 1.1 | 0.9
3916 | 'LOGAN CR ' | 230 | 1 | 2 | 2 | 1 | 1.0222 | -9.9548 | 1.1 | 0.9 | 1.1 | 0.9
3917 | 'LOSBANOS ' | 230 | 1 | 2 | 2 | 1 | 1.0101 | -8.3354 | 1.1 | 0.9 | 1.1 | 0.9
3918 | 'MOSSLAND ' | 230 | 1 | 2 | 2 | 1 | 0.99384 | -6.0267 | 1.1 | 0.9 | 1.1 | 0.9
3919 | 'PALERMO ' | 230 | 1 | 2 | 2 | 1 | 0.99679 | -16.618 | 1.1 | 0.9 | 1.1 | 0.9
3920 | 'RIO OSO ' | 230 | 1 | 2 | 2 | 1 | 0.99025 | -16.2913 | 1.1 | 0.9 | 1.1 | 0.9
3921 | 'ROUND MT ' | 230 | 1 | 2 | 2 | 1 | 1.07 | 1.5011 | 1.1 | 0.9 | 1.1 | 0.9
3922 | 'TABLE MT ' | 230 | 1 | 2 | 2 | 1 | 1.0163 | -12.7252 | 1.1 | 0.9 | 1.1 | 0.9
3923 | 'TESLA ' | 230 | 1 | 2 | 2 | 1 | 1.0176 | -1.025 | 1.1 | 0.9 | 1.1 | 0.9
3924 | 'VACA-DIX ' | 230 | 1 | 2 | 2 | 1 | 1.0095 | -5.4562 | 1.1 | 0.9 | 1.1 | 0.9
3925 | 'COTWDPGE ' | 115 | 1 | 2 | 2 | 1 | 1.0299 | -4.0766 | 1.1 | 0.9 | 1.1 | 0.9
3926 | 'RIO OSO ' | 115 | 1 | 2 | 2 | 1 | 0.99786 | -19.5525 | 1.1 | 0.9 | 1.1 | 0.9
3931 | 'ROUND MT ' | 20 | 2 | 2 | 2 | 1 | 1.0707 | 1.8629 | 1.1 | 0.9 | 1.1 | 0.9
3932 | 'MOSSLAND ' | 20 | 2 | 2 | 2 | 1 | 0.99876 | -1.8746 | 1.1 | 0.9 | 1.1 | 0.9
3933 | 'TESLA ' | 20 | 3 | 2 | 2 | 1 | 1.02 | 0 | 1.1 | 0.9 | 1.1 | 0.9
4001 | 'MALIN ' | 500 | 1 | 3 | 11 | 1 | 1.08 | -5.9328 | 1.1 | 0.9 | 1.1 | 0.9
4002 | 'SUMMER L ' | 500 | 1 | 3 | 11 | 1 | 1.1141 | -3.7122 | 1.1 | 0.9 | 1.1 | 0.9
4003 | 'BURNS ' | 500 | 1 | 3 | 11 | 1 | 1.1283 | 4.1039 | 1.1 | 0.9 | 1.1 | 0.9
4004 | 'GRIZZLY ' | 500 | 1 | 3 | 11 | 1 | 1.1013 | -5.7208 | 1.1 | 0.9 | 1.1 | 0.9
4005 | 'JOHN DAY ' | 500 | 1 | 3 | 11 | 1 | 1.08 | -5.3425 | 1.1 | 0.9 | 1.1 | 0.9
4006 | 'BIG EDDY ' | 500 | 1 | 3 | 11 | 1 | 1.0759 | -8.9606 | 1.1 | 0.9 | 1.1 | 0.9
4007 | 'CELILOCA ' | 500 | 1 | 3 | 11 | 1 | 1.0759 | -9.1337 | 1.1 | 0.9 | 1.1 | 0.9
4008 | 'MALIN ' | 345 | 1 | 3 | 11 | 1 | 1.0801 | -8.1151 | 1.1 | 0.9 | 1.1 | 0.9
4009 | 'BIG EDDY ' | 230 | 1 | 3 | 11 | 1 | 1.08 | -11.4341 | 1.1 | 0.9 | 1.1 | 0.9
4010 | 'CELILO ' | 230 | 1 | 3 | 11 | 1 | 1.0787 | -11.6748 | 1.1 | 0.9 | 1.1 | 0.9
4031 | 'MALIN ' | 20 | 2 | 3 | 11 | 1 | 1.0769 | -5.5496 | 1.1 | 0.9 | 1.1 | 0.9
4035 | 'JOHN DAY ' | 20 | 2 | 3 | 11 | 1 | 1.0777 | -4.7798 | 1.1 | 0.9 | 1.1 | 0.9
4039 | 'DALLES21 ' | 20 | 2 | 3 | 13 | 1 | 1.0839 | -10.8846 | 1.1 | 0.9 | 1.1 | 0.9
4090 | 'MALIN1 ' | 500 | 1 | 3 | 11 | 1 | 1.1107 | -4.0346 | 1.1 | 0.9 | 1.1 | 0.9
4091 | 'GRIZZLY1 ' | 500 | 1 | 3 | 11 | 1 | 1.1106 | -4.8922 | 1.1 | 0.9 | 1.1 | 0.9
4092 | 'GRIZZLY2 ' | 500 | 1 | 3 | 11 | 1 | 1.0941 | -5.9281 | 1.1 | 0.9 | 1.1 | 0.9
4093 | 'GRIZZLY3 ' | 500 | 1 | 3 | 11 | 1 | 1.0923 | -5.9578 | 1.1 | 0.9 | 1.1 | 0.9
4094 | 'GRIZZLY4 ' | 500 | 1 | 3 | 11 | 1 | 1.1059 | -5.7326 | 1.1 | 0.9 | 1.1 | 0.9
4095 | 'GRIZZLY5 ' | 500 | 1 | 3 | 11 | 1 | 1.0924 | -5.9401 | 1.1 | 0.9 | 1.1 | 0.9
4096 | 'GRIZZLY6 ' | 500 | 1 | 3 | 11 | 1 | 1.0904 | -5.9721 | 1.1 | 0.9 | 1.1 | 0.9
4097 | 'GRIZZLY7 ' | 500 | 1 | 3 | 11 | 1 | 1.1057 | -5.7303 | 1.1 | 0.9 | 1.1 | 0.9
4101 | 'COULEE ' | 500 | 1 | 3 | 13 | 1 | 1.128 | 11.2675 | 1.1 | 0.9 | 1.1 | 0.9
4102 | 'HANFORD ' | 500 | 1 | 3 | 13 | 1 | 1.096 | 3.9997 | 1.1 | 0.9 | 1.1 | 0.9
4103 | 'BELL ' | 500 | 1 | 3 | 13 | 1 | 1.0808 | -3.7392 | 1.1 | 0.9 | 1.1 | 0.9
4104 | 'BELL ' | 230 | 1 | 3 | 13 | 1 | 1.0518 | -14.7065 | 1.1 | 0.9 | 1.1 | 0.9
4131 | 'COULEE ' | 20 | 2 | 3 | 13 | 1 | 1.131 | 13.1595 | 1.1 | 0.9 | 1.1 | 0.9
4132 | 'HANFORD ' | 20 | 2 | 3 | 13 | 1 | 1.0965 | 5.6353 | 1.1 | 0.9 | 1.1 | 0.9
4201 | 'NORTH ' | 500 | 1 | 3 | 13 | 1 | 1.12 | 4.0883 | 1.1 | 0.9 | 1.1 | 0.9
4202 | 'WCASCADE ' | 500 | 1 | 3 | 13 | 1 | 1.06 | -8.249 | 1.1 | 0.9 | 1.1 | 0.9
4203 | 'WILLAMET ' | 500 | 1 | 3 | 13 | 1 | 1.0293 | -11.4988 | 1.1 | 0.9 | 1.1 | 0.9
4204 | 'MERIDIAN ' | 500 | 1 | 3 | 13 | 1 | 1.0619 | -7.7302 | 1.1 | 0.9 | 1.1 | 0.9
4231 | 'NORTH G3 ' | 20 | 2 | 3 | 13 | 1 | 1.1263 | 5.0125 | 1.1 | 0.9 | 1.1 | 0.9
4232 | 'WCASCADE ' | 20 | 2 | 3 | 13 | 1 | 1.0599 | -8.0228 | 1.1 | 0.9 | 1.1 | 0.9
5001 | 'CANADA ' | 500 | 1 | 3 | 4 | 1 | 1.05 | -5.7602 | 1.1 | 0.9 | 1.1 | 0.9
5002 | 'CANALB ' | 500 | 1 | 3 | 1 | 1 | 1.055 | -6.9724 | 1.1 | 0.9 | 1.1 | 0.9
5003 | 'CA230TO ' | 230 | 1 | 3 | 1 | 1 | 1.0537 | -10.449 | 1.1 | 0.9 | 1.1 | 0.9
5004 | 'CA230 ' | 230 | 1 | 3 | 4 | 1 | 1.0868 | -12.6232 | 1.1 | 0.9 | 1.1 | 0.9
5031 | 'CANAD G1 ' | 20 | 2 | 3 | 4 | 1 | 1.0546 | -4.0013 | 1.1 | 0.9 | 1.1 | 0.9
5032 | 'CMAIN GM ' | 20 | 2 | 3 | 1 | 1 | 1.0614 | -4.5562 | 1.1 | 0.9 | 1.1 | 0.9
6101 | 'MIDPOINT ' | 500 | 1 | 3 | 6 | 1 | 1.0662 | 13.9305 | 1.1 | 0.9 | 1.1 | 0.9
6102 | 'MIDPOINT ' | 345 | 1 | 3 | 6 | 1 | 1.03 | 16.7065 | 1.1 | 0.9 | 1.1 | 0.9
6103 | 'BORAH ' | 345 | 1 | 3 | 6 | 1 | 1.0155 | 14.8856 | 1.1 | 0.9 | 1.1 | 0.9
6104 | 'BORAH ' | 230 | 1 | 3 | 6 | 1 | 1.0098 | 2.6761 | 1.1 | 0.9 | 1.1 | 0.9
6132 | 'MIDPOINT ' | 20 | 2 | 3 | 6 | 1 | 1.0257 | 17.7272 | 1.1 | 0.9 | 1.1 | 0.9
6201 | 'COLSTRP ' | 500 | 1 | 3 | 8 | 1 | 1.06 | 7.3626 | 1.1 | 0.9 | 1.1 | 0.9
6202 | 'GARRISON ' | 500 | 1 | 3 | 8 | 1 | 1.0948 | 2.7322 | 1.1 | 0.9 | 1.1 | 0.9
6203 | 'COLSTRP ' | 230 | 1 | 3 | 8 | 1 | 1.0057 | 6.4631 | 1.1 | 0.9 | 1.1 | 0.9
6204 | 'GARRISON ' | 230 | 1 | 3 | 8 | 1 | 1.0517 | 3.1248 | 1.1 | 0.9 | 1.1 | 0.9
6205 | 'MONTANA ' | 230 | 1 | 3 | 8 | 1 | 1.05 | 13.0019 | 1.1 | 0.9 | 1.1 | 0.9
6231 | 'COLSTRP ' | 20 | 2 | 3 | 8 | 1 | 1.0592 | 7.5999 | 1.1 | 0.9 | 1.1 | 0.9
6235 | 'MONTA G1 ' | 20 | 2 | 3 | 8 | 1 | 1.0507 | 13.3683 | 1.1 | 0.9 | 1.1 | 0.9
6301 | 'BRIDGER ' | 345 | 1 | 3 | 14 | 1 | 1.0177 | 16.19 | 1.1 | 0.9 | 1.1 | 0.9
6302 | 'LARAMIE ' | 345 | 1 | 3 | 14 | 1 | 1.0069 | -32.2769 | 1.1 | 0.9 | 1.1 | 0.9
6303 | 'BRIDGER2 ' | 230 | 1 | 3 | 14 | 1 | 1.03 | 29.5363 | 1.1 | 0.9 | 1.1 | 0.9
6304 | 'LARAMIE ' | 230 | 1 | 3 | 14 | 1 | 0.99528 | -19.7357 | 1.1 | 0.9 | 1.1 | 0.9
6305 | 'NAUGHTON ' | 230 | 1 | 3 | 14 | 1 | 1.06 | 29.9977 | 1.1 | 0.9 | 1.1 | 0.9
6333 | 'BRIDGER ' | 20 | 2 | 3 | 14 | 1 | 1.033 | 30.548 | 1.1 | 0.9 | 1.1 | 0.9
6335 | 'NAUGHT ' | 20 | 2 | 3 | 14 | 1 | 1.0636 | 30.7165 | 1.1 | 0.9 | 1.1 | 0.9
6401 | 'TRACYSPP ' | 345 | 1 | 1 | 9 | 1 | 1.0724 | -19.1477 | 1.1 | 0.9 | 1.1 | 0.9
6402 | 'SUMITSPP ' | 115 | 1 | 1 | 9 | 1 | 1.0358 | -21.0055 | 1.1 | 0.9 | 1.1 | 0.9
6403 | 'VALMY ' | 345 | 1 | 1 | 9 | 1 | 1.11 | 4.0155 | 1.1 | 0.9 | 1.1 | 0.9
6404 | 'GONDER ' | 345 | 1 | 1 | 9 | 1 | 1.0819 | -4.0766 | 1.1 | 0.9 | 1.1 | 0.9
6433 | 'VALMY ' | 20 | 2 | 1 | 9 | 1 | 1.1112 | 4.3221 | 1.1 | 0.9 | 1.1 | 0.9
6501 | 'BENLOMND ' | 345 | 1 | 3 | 12 | 1 | 1.0223 | -0.4241 | 1.1 | 0.9 | 1.1 | 0.9
6502 | 'CAMP WIL ' | 345 | 1 | 3 | 12 | 1 | 1.0202 | -1.1806 | 1.1 | 0.9 | 1.1 | 0.9
6503 | 'EMERY ' | 345 | 1 | 3 | 12 | 1 | 1.065 | 10.2234 | 1.1 | 0.9 | 1.1 | 0.9
6504 | 'MONA ' | 345 | 1 | 3 | 12 | 1 | 1.0228 | -1.1804 | 1.1 | 0.9 | 1.1 | 0.9
6505 | 'PINTO ' | 345 | 1 | 3 | 12 | 1 | 1.0714 | 8.8513 | 1.1 | 0.9 | 1.1 | 0.9
6506 | 'PINTO PS ' | 345 | 1 | 3 | 12 | 1 | 1.059 | 8.6263 | 1.1 | 0.9 | 1.1 | 0.9
6507 | 'SIGURD ' | 345 | 1 | 3 | 12 | 1 | 1.0513 | 0.2894 | 1.1 | 0.9 | 1.1 | 0.9
6508 | 'SPAN FRK ' | 345 | 1 | 3 | 12 | 1 | 1.0282 | 1.5377 | 1.1 | 0.9 | 1.1 | 0.9
6509 | 'TERMINAL ' | 345 | 1 | 3 | 12 | 1 | 1.021 | -1.1618 | 1.1 | 0.9 | 1.1 | 0.9
6510 | 'BENLOMND ' | 230 | 1 | 3 | 12 | 1 | 0.98849 | 0.3377 | 1.1 | 0.9 | 1.1 | 0.9
6533 | 'EMERY ' | 20 | 2 | 3 | 12 | 1 | 1.0664 | 11.0672 | 1.1 | 0.9 | 1.1 | 0.9
7001 | 'COLOEAST ' | 345 | 1 | 3 | 5 | 1 | 1.02 | -33.8246 | 1.1 | 0.9 | 1.1 | 0.9
7002 | 'CRAIG ' | 345 | 1 | 3 | 5 | 1 | 1.015 | -30.6709 | 1.1 | 0.9 | 1.1 | 0.9
7031 | 'COLOEAST ' | 20 | 2 | 3 | 5 | 1 | 1.0262 | -32.574 | 1.1 | 0.9 | 1.1 | 0.9
7032 | 'CRAIG ' | 20 | 2 | 3 | 5 | 1 | 1.0153 | -29.9099 | 1.1 | 0.9 | 1.1 | 0.9
8001 | 'OLINDA ' | 500 | 1 | 2 | 2 | 1 | 1.0648 | -6.0412 | 1.1 | 0.9 | 1.1 | 0.9
8002 | 'TRACY ' | 500 | 1 | 2 | 2 | 1 | 1.042 | -7.7367 | 1.1 | 0.9 | 1.1 | 0.9
8003 | 'COTWDWAP ' | 230 | 1 | 2 | 2 | 1 | 1.075 | -3.4806 | 1.1 | 0.9 | 1.1 | 0.9
8004 | 'RNCHSECO ' | 230 | 1 | 2 | 2 | 1 | 1 | -11.7273 | 1.1 | 0.9 | 1.1 | 0.9
8005 | 'TRACYPMP ' | 230 | 1 | 2 | 2 | 1 | 1.003 | -13.4174 | 1.1 | 0.9 | 1.1 | 0.9
8033 | 'COTWDWAP ' | 20 | 2 | 2 | 2 | 1 | 1.0762 | -3.1879 | 1.1 | 0.9 | 1.1 | 0.9
8034 | 'RNCHSECO ' | 20 | 2 | 2 | 2 | 1 | 1.0023 | -10.7632 | 1.1 | 0.9 | 1.1 | 0.9
0 / END OF BUS DATA | BEGIN LOAD DATA
@! I | 'ID' | STAT | AREA | ZONE | PL | QL | IP | IQ | YP | YQ | OWNER | SCALE | INTRPT | DGENP | DGENQ | DGENF
1002 | '1 ' | 1 | 1 | 3 | 0 | 0 | 223.71 | 0 | 0 | 583.546 | 1 | 1 | 0 | 0 | 0 | 0
1003 | '1 ' | 1 | 1 | 10 | 0 | 0 | 2212.664 | 0 | 0 | -387.354 | 1 | 1 | 0 | 0 | 0 | 0
1004 | '1 ' | 1 | 1 | 10 | 0 | 0 | 1007.718 | 0 | 0 | -5.204 | 1 | 1 | 0 | 0 | 0 | 0
1101 | '1 ' | 1 | 1 | 3 | 0 | 0 | 4482.541 | 0 | 0 | 134.344 | 1 | 1 | 0 | 0 | 0 | 0
1102 | '1 ' | 1 | 1 | 3 | 0 | 0 | 179.873 | 0 | 0 | -23.907 | 1 | 1 | 0 | 0 | 0 | 0
1201 | '1 ' | 1 | 1 | 3 | 0 | 0 | 153.984 | 0 | 0 | 1.711 | 1 | 1 | 0 | 0 | 0 | 0
1202 | '1 ' | 1 | 1 | 3 | 0 | 0 | 810.75 | 0 | 0 | -246.169 | 1 | 1 | 0 | 0 | 0 | 0
1301 | '1 ' | 1 | 1 | 3 | 0 | 0 | 2588.305 | 0 | 0 | -323.093 | 1 | 1 | 0 | 0 | 0 | 0
1302 | '1 ' | 1 | 1 | 9 | 0 | 0 | 17.088 | 0 | 0 | -2.183 | 1 | 1 | 0 | 0 | 0 | 0
1303 | '1 ' | 1 | 1 | 9 | 0 | 0 | 6204.116 | 0 | 0 | -805.276 | 1 | 1 | 0 | 0 | 0 | 0
1401 | '1 ' | 1 | 1 | 3 | 0 | 0 | 6314.529 | 0 | 0 | -1423.225 | 1 | 1 | 0 | 0 | 0 | 0
1402 | '1 ' | 1 | 1 | 3 | 0 | 0 | 5074.202 | 0 | 0 | 536.538 | 1 | 1 | 0 | 0 | 0 | 0
2000 | '1 ' | 1 | 4 | 7 | 0 | 0 | 2207.188 | 0 | 0 | -287.916 | 1 | 1 | 0 | 0 | 0 | 0
2100 | '1 ' | 1 | 2 | 2 | 0 | 0 | 244.479 | 0 | 0 | -46.066 | 1 | 1 | 0 | 0 | 0 | 0
2202 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1413.957 | 0 | 0 | -249.625 | 1 | 1 | 0 | 0 | 0 | 0
2203 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1530.047 | 0 | 0 | -247.96 | 1 | 1 | 0 | 0 | 0 | 0
2400 | '1 ' | 1 | 2 | 2 | 0 | 0 | 741.606 | 0 | 0 | -65.877 | 1 | 1 | 0 | 0 | 0 | 0
2401 | '1 ' | 1 | 2 | 2 | 0 | 0 | 756.558 | 0 | 0 | -85.945 | 1 | 1 | 0 | 0 | 0 | 0
2402 | '1 ' | 1 | 2 | 2 | 0 | 0 | 944.185 | 0 | 0 | -69.616 | 1 | 1 | 0 | 0 | 0 | 0
2403 | '1 ' | 1 | 2 | 2 | 0 | 0 | 924.912 | 0 | 0 | -33.229 | 1 | 1 | 0 | 0 | 0 | 0
2405 | '1 ' | 1 | 2 | 2 | 0 | 0 | 734.331 | 0 | 0 | -20.175 | 1 | 1 | 0 | 0 | 0 | 0
2406 | '1 ' | 1 | 2 | 2 | 0 | 0 | 659.215 | 0 | 0 | 36.185 | 1 | 1 | 0 | 0 | 0 | 0
2407 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1610.419 | 0 | 0 | 35.064 | 1 | 1 | 0 | 0 | 0 | 0
2408 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1554.955 | 0 | 0 | 64.2 | 1 | 1 | 0 | 0 | 0 | 0
2409 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1413.334 | 0 | 0 | 74.998 | 1 | 1 | 0 | 0 | 0 | 0
2410 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1411.456 | 0 | 0 | -51.802 | 1 | 1 | 0 | 0 | 0 | 0
2411 | '1 ' | 1 | 2 | 2 | 0 | 0 | 959.465 | 0 | 0 | -65.677 | 1 | 1 | 0 | 0 | 0 | 0
2502 | '1 ' | 1 | 2 | 2 | 0 | 0 | 2087.843 | 0 | 0 | 79.306 | 1 | 1 | 0 | 0 | 0 | 0
2503 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1646.515 | 0 | 0 | -178.564 | 1 | 1 | 0 | 0 | 0 | 0
2600 | '1 ' | 1 | 2 | 2 | 0 | 0 | -1591.978 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
2602 | '1 ' | 1 | 2 | 2 | 0 | 0 | 87.531 | 0 | 0 | -11.19 | 1 | 1 | 0 | 0 | 0 | 0
2604 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1791.945 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
2608 | '1 ' | 1 | 2 | 2 | 0 | 0 | 88.03 | 0 | 0 | -11.318 | 1 | 1 | 0 | 0 | 0 | 0
2609 | '1 ' | 1 | 2 | 2 | 0 | 0 | 120.79 | 0 | 0 | -24.191 | 1 | 1 | 0 | 0 | 0 | 0
2610 | '1 ' | 1 | 2 | 2 | 0 | 0 | 88.994 | 0 | 0 | -11.567 | 1 | 1 | 0 | 0 | 0 | 0
2611 | '1 ' | 1 | 2 | 2 | 0 | 0 | 88.03 | 0 | 0 | -11.318 | 1 | 1 | 0 | 0 | 0 | 0
2612 | '1 ' | 1 | 2 | 2 | 0 | 0 | 106.667 | 0 | 0 | -21.743 | 1 | 1 | 0 | 0 | 0 | 0
2613 | '1 ' | 1 | 2 | 2 | 0 | 0 | 287.725 | 0 | 0 | -58.812 | 1 | 1 | 0 | 0 | 0 | 0
2614 | '1 ' | 1 | 2 | 2 | 0 | 0 | 123.152 | 0 | 0 | -24.956 | 1 | 1 | 0 | 0 | 0 | 0
2615 | '1 ' | 1 | 2 | 2 | 0 | 0 | 718.654 | 0 | 0 | -117.014 | 1 | 1 | 0 | 0 | 0 | 0
2616 | '1 ' | 1 | 2 | 2 | 0 | 0 | 104.99 | 0 | 0 | -21.629 | 1 | 1 | 0 | 0 | 0 | 0
2617 | '1 ' | 1 | 2 | 2 | 0 | 0 | 108.473 | 0 | 0 | -22.485 | 1 | 1 | 0 | 0 | 0 | 0
2618 | '1 ' | 1 | 2 | 2 | 0 | 0 | 784.705 | 0 | 0 | 5.422 | 1 | 1 | 0 | 0 | 0 | 0
2619 | '1 ' | 1 | 2 | 2 | 0 | 0 | -2466.528 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
2620 | '1 ' | 1 | 2 | 2 | 0 | 0 | 181.756 | 0 | 0 | -15.454 | 1 | 1 | 0 | 0 | 0 | 0
2621 | '1 ' | 1 | 2 | 2 | 0 | 0 | 209.415 | 0 | 0 | 55.132 | 1 | 1 | 0 | 0 | 0 | 0
3101 | '1 ' | 1 | 2 | 2 | 0 | 0 | 313.58 | 0 | 0 | -49.549 | 1 | 1 | 0 | 0 | 0 | 0
3102 | '1 ' | 1 | 2 | 2 | 0 | 0 | 145.724 | 0 | 0 | -23.131 | 1 | 1 | 0 | 0 | 0 | 0
3103 | '1 ' | 1 | 2 | 2 | 0 | 0 | 380.419 | 0 | 0 | -54.591 | 1 | 1 | 0 | 0 | 0 | 0
3104 | '1 ' | 1 | 2 | 2 | 0 | 0 | 283.512 | 0 | 0 | -37.304 | 1 | 1 | 0 | 0 | 0 | 0
3105 | '1 ' | 1 | 2 | 2 | 0 | 0 | 215.372 | 0 | 0 | -44.182 | 1 | 1 | 0 | 0 | 0 | 0
3201 | '1 ' | 1 | 2 | 2 | 0 | 0 | 417.176 | 0 | 0 | -88.465 | 1 | 1 | 0 | 0 | 0 | 0
3202 | '1 ' | 1 | 2 | 2 | 0 | 0 | 528.943 | 0 | 0 | -75.52 | 1 | 1 | 0 | 0 | 0 | 0
3203 | '1 ' | 1 | 2 | 2 | 0 | 0 | 592.543 | 0 | 0 | -143.183 | 1 | 1 | 0 | 0 | 0 | 0
3204 | '1 ' | 1 | 2 | 2 | 0 | 0 | 595.949 | 0 | 0 | -84.091 | 1 | 1 | 0 | 0 | 0 | 0
3205 | '1 ' | 1 | 2 | 2 | 0 | 0 | 492.201 | 0 | 0 | -70.216 | 1 | 1 | 0 | 0 | 0 | 0
3302 | '1 ' | 1 | 2 | 2 | 0 | 0 | 316.377 | 0 | 0 | -80.011 | 1 | 1 | 0 | 0 | 0 | 0
3303 | '1 ' | 1 | 2 | 2 | 0 | 0 | 562.87 | 0 | 0 | -135.643 | 1 | 1 | 0 | 0 | 0 | 0
3304 | '1 ' | 1 | 2 | 2 | 0 | 0 | 485.777 | 0 | 0 | -112.963 | 1 | 1 | 0 | 0 | 0 | 0
3305 | '1 ' | 1 | 2 | 2 | 0 | 0 | 389.689 | 0 | 0 | -55.787 | 1 | 1 | 0 | 0 | 0 | 0
3401 | '1 ' | 1 | 2 | 2 | 0 | 0 | 523.259 | 0 | 0 | -132.931 | 1 | 1 | 0 | 0 | 0 | 0
3403 | '1 ' | 1 | 2 | 2 | 0 | 0 | 464.372 | 0 | 0 | -66.225 | 1 | 1 | 0 | 0 | 0 | 0
3404 | '1 ' | 1 | 2 | 2 | 0 | 0 | 400.37 | 0 | 0 | -57.509 | 1 | 1 | 0 | 0 | 0 | 0
3405 | '1 ' | 1 | 2 | 2 | 0 | 0 | 423.026 | 0 | 0 | -62.878 | 1 | 1 | 0 | 0 | 0 | 0
3501 | '1 ' | 1 | 2 | 2 | 0 | 0 | 562.514 | 0 | 0 | -80.114 | 1 | 1 | 0 | 0 | 0 | 0
3601 | '1 ' | 1 | 2 | 2 | 0 | 0 | 92.975 | 0 | 0 | -12.968 | 1 | 1 | 0 | 0 | 0 | 0
3701 | '1 ' | 1 | 1 | 9 | 0 | 0 | 317.051 | 0 | 0 | -15.847 | 1 | 1 | 0 | 0 | 0 | 0
3801 | '1 ' | 1 | 2 | 2 | 0 | 0 | 164.062 | 0 | 0 | -38.776 | 1 | 1 | 0 | 0 | 0 | 0
3804 | '1 ' | 1 | 2 | 2 | 0 | 0 | 201.824 | 0 | 0 | -50.058 | 1 | 1 | 0 | 0 | 0 | 0
3805 | '1 ' | 1 | 2 | 2 | 0 | 0 | 434.251 | 0 | 0 | -137.035 | 1 | 1 | 0 | 0 | 0 | 0
3806 | '1 ' | 1 | 2 | 2 | 0 | 0 | 255.767 | 0 | 0 | -35.854 | 1 | 1 | 0 | 0 | 0 | 0
3902 | '1 ' | 1 | 2 | 2 | 0 | 0 | 137.692 | 0 | 0 | -34.423 | 1 | 1 | 0 | 0 | 0 | 0
3903 | '1 ' | 1 | 2 | 2 | 0 | 0 | 190.745 | 0 | 0 | -26.909 | 1 | 1 | 0 | 0 | 0 | 0
3907 | '1 ' | 1 | 2 | 2 | 0 | 0 | 430.38 | 0 | 0 | -60.984 | 1 | 1 | 0 | 0 | 0 | 0
3908 | '1 ' | 1 | 2 | 2 | 0 | 0 | 186.87 | 0 | 0 | -23.908 | 1 | 1 | 0 | 0 | 0 | 0
3909 | '1 ' | 1 | 2 | 2 | 0 | 0 | 159.388 | 0 | 0 | -38.425 | 1 | 1 | 0 | 0 | 0 | 0
3910 | '1 ' | 1 | 2 | 2 | 0 | 0 | 228.437 | 0 | 0 | -34.143 | 1 | 1 | 0 | 0 | 0 | 0
3911 | '1 ' | 1 | 2 | 2 | 0 | 0 | 204.367 | 0 | 0 | -40.227 | 1 | 1 | 0 | 0 | 0 | 0
3912 | '1 ' | 1 | 2 | 2 | 0 | 0 | 156.919 | 0 | 0 | 0.57 | 1 | 1 | 0 | 0 | 0 | 0
3913 | '1 ' | 1 | 2 | 2 | 0 | 0 | 301.003 | 0 | 0 | -40.262 | 1 | 1 | 0 | 0 | 0 | 0
3914 | '1 ' | 1 | 2 | 2 | 0 | 0 | 207.245 | 0 | 0 | -48.345 | 1 | 1 | 0 | 0 | 0 | 0
3915 | '1 ' | 1 | 2 | 2 | 0 | 0 | 230.849 | 0 | 0 | -48.836 | 1 | 1 | 0 | 0 | 0 | 0
3916 | '1 ' | 1 | 2 | 2 | 0 | 0 | 139.766 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
3917 | '1 ' | 1 | 2 | 2 | 0 | 0 | 214.158 | 0 | 0 | -39.517 | 1 | 1 | 0 | 0 | 0 | 0
3918 | '1 ' | 1 | 2 | 2 | 0 | 0 | 289.544 | 0 | 0 | -68.957 | 1 | 1 | 0 | 0 | 0 | 0
3919 | '1 ' | 1 | 2 | 2 | 0 | 0 | 171.67 | 0 | 0 | -23.175 | 1 | 1 | 0 | 0 | 0 | 0
3920 | '1 ' | 1 | 2 | 2 | 0 | 0 | 158.827 | 0 | 0 | -22.302 | 1 | 1 | 0 | 0 | 0 | 0
3921 | '1 ' | 1 | 2 | 2 | 0 | 0 | 126.917 | 0 | 0 | -27.373 | 1 | 1 | 0 | 0 | 0 | 0
3922 | '1 ' | 1 | 2 | 2 | 0 | 0 | 231.814 | 0 | 0 | -29.67 | 1 | 1 | 0 | 0 | 0 | 0
3923 | '1 ' | 1 | 2 | 2 | 0 | 0 | 353.452 | 0 | 0 | -58.418 | 1 | 1 | 0 | 0 | 0 | 0
3924 | '1 ' | 1 | 2 | 2 | 0 | 0 | 300.147 | 0 | 0 | -42.707 | 1 | 1 | 0 | 0 | 0 | 0
3926 | '1 ' | 1 | 2 | 2 | 0 | 0 | 244.214 | 0 | 0 | -15.453 | 1 | 1 | 0 | 0 | 0 | 0
4002 | '1 ' | 1 | 3 | 11 | 0 | 0 | 154.505 | 0 | 0 | -18.455 | 1 | 1 | 0 | 0 | 0 | 0
4004 | '1 ' | 1 | 3 | 11 | 0 | 0 | 248.18 | 0 | 0 | -29.723 | 1 | 1 | 0 | 0 | 0 | 0
4005 | '1 ' | 1 | 3 | 11 | 0 | 0 | 444.55 | 0 | 0 | -134.961 | 1 | 1 | 0 | 0 | 0 | 0
4008 | '1 ' | 1 | 3 | 11 | 0 | 0 | 265.108 | 0 | 0 | -32.154 | 1 | 1 | 0 | 0 | 0 | 0
4009 | '1 ' | 1 | 3 | 11 | 0 | 0 | 2045.132 | 0 | 0 | -369.852 | 1 | 1 | 0 | 0 | 0 | 0
4010 | '1 ' | 1 | 3 | 11 | 0 | 0 | 2904.493 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
4101 | '1 ' | 1 | 3 | 13 | 0 | 0 | 882.117 | 0 | 0 | -102.001 | 1 | 1 | 0 | 0 | 0 | 0
4102 | '1 ' | 1 | 3 | 13 | 0 | 0 | 438.548 | 0 | 0 | -57.162 | 1 | 1 | 0 | 0 | 0 | 0
4103 | '1 ' | 1 | 3 | 13 | 0 | 0 | 10.805 | 0 | 0 | -1.303 | 1 | 1 | 0 | 0 | 0 | 0
4104 | '1 ' | 1 | 3 | 13 | 0 | 0 | 2424.986 | 0 | 0 | -303.469 | 1 | 1 | 0 | 0 | 0 | 0
4201 | '1 ' | 1 | 3 | 13 | 0 | 0 | 5145.231 | 0 | 0 | -367.517 | 1 | 1 | 0 | 0 | 0 | 0
4202 | '1 ' | 1 | 3 | 13 | 0 | 0 | 4300.226 | 0 | 0 | -529.215 | 1 | 1 | 0 | 0 | 0 | 0
4203 | '1 ' | 1 | 3 | 13 | 0 | 0 | 4308.429 | 0 | 0 | -552.906 | 1 | 1 | 0 | 0 | 0 | 0
4204 | '1 ' | 1 | 3 | 13 | 0 | 0 | 949.629 | 0 | 0 | -115.952 | 1 | 1 | 0 | 0 | 0 | 0
5001 | '1 ' | 1 | 3 | 4 | 0 | 0 | 7213.383 | 0 | 0 | -1561.338 | 1 | 1 | 0 | 0 | 0 | 0
5002 | '1 ' | 1 | 3 | 1 | 0 | 0 | 8534.582 | 0 | 0 | -1055.106 | 1 | 1 | 0 | 0 | 0 | 0
5003 | '1 ' | 1 | 3 | 1 | 0 | 0 | 589.263 | 0 | 0 | -73.624 | 1 | 1 | 0 | 0 | 0 | 0
6102 | '1 ' | 1 | 3 | 6 | 0 | 0 | 1022.47 | 0 | 0 | 325.457 | 1 | 1 | 0 | 0 | 0 | 0
6103 | '1 ' | 1 | 3 | 6 | 0 | 0 | 386.454 | 0 | 0 | -49.703 | 1 | 1 | 0 | 0 | 0 | 0
6104 | '1 ' | 1 | 3 | 6 | 0 | 0 | 1683.648 | 0 | 0 | -218.144 | 1 | 1 | 0 | 0 | 0 | 0
6201 | '1 ' | 1 | 3 | 8 | 0 | 0 | 194.17 | 0 | 0 | -23.903 | 1 | 1 | 0 | 0 | 0 | 0
6202 | '1 ' | 1 | 3 | 8 | 0 | 0 | 81.319 | 0 | 0 | -11.365 | 1 | 1 | 0 | 0 | 0 | 0
6203 | '1 ' | 1 | 3 | 8 | 0 | 0 | 609.243 | 0 | 0 | -143.626 | 1 | 1 | 0 | 0 | 0 | 0
6204 | '1 ' | 1 | 3 | 8 | 0 | 0 | 667.55 | 0 | 0 | -142.578 | 1 | 1 | 0 | 0 | 0 | 0
6205 | '1 ' | 1 | 3 | 8 | 0 | 0 | 465.984 | 0 | 0 | -78.317 | 1 | 1 | 0 | 0 | 0 | 0
6301 | '1 ' | 1 | 3 | 14 | 0 | 0 | 508.649 | 0 | 0 | -65.361 | 1 | 1 | 0 | 0 | 0 | 0
6302 | '1 ' | 1 | 3 | 14 | 0 | 0 | 588.418 | 0 | 0 | -76.334 | 1 | 1 | 0 | 0 | 0 | 0
6303 | '1 ' | 1 | 3 | 14 | 0 | 0 | 724.856 | 0 | 0 | -91.813 | 1 | 1 | 0 | 0 | 0 | 0
6305 | '1 ' | 1 | 3 | 14 | 0 | 0 | 56.823 | 0 | 0 | -17.579 | 1 | 1 | 0 | 0 | 0 | 0
6401 | '1 ' | 1 | 1 | 9 | 0 | 0 | 1628.39 | 0 | 0 | -206.824 | 1 | 1 | 0 | 0 | 0 | 0
6402 | '1 ' | 1 | 1 | 9 | 0 | 0 | 270.855 | 0 | 0 | -35.135 | 1 | 1 | 0 | 0 | 0 | 0
6403 | '1 ' | 1 | 1 | 9 | 0 | 0 | 1.98 | 0 | 0 | -0.221 | 1 | 1 | 0 | 0 | 0 | 0
6404 | '1 ' | 1 | 1 | 9 | 0 | 0 | 27.498 | 0 | 0 | -3.399 | 1 | 1 | 0 | 0 | 0 | 0
6501 | '1 ' | 1 | 3 | 12 | 0 | 0 | 193.033 | 0 | 0 | -62.491 | 1 | 1 | 0 | 0 | 0 | 0
6502 | '1 ' | 1 | 3 | 12 | 0 | 0 | 1539.327 | 0 | 0 | -271.901 | 1 | 1 | 0 | 0 | 0 | 0
6503 | '1 ' | 1 | 3 | 12 | 0 | 0 | 414.228 | 0 | 0 | -127.491 | 1 | 1 | 0 | 0 | 0 | 0
6504 | '1 ' | 1 | 3 | 12 | 0 | 0 | 293.725 | 0 | 0 | -37.889 | 1 | 1 | 0 | 0 | 0 | 0
6505 | '1 ' | 1 | 3 | 12 | 0 | 0 | 6.555 | 0 | 0 | -2.076 | 1 | 1 | 0 | 0 | 0 | 0
6507 | '1 ' | 1 | 3 | 12 | 0 | 0 | 527.834 | 0 | 0 | 58.453 | 1 | 1 | 0 | 0 | 0 | 0
6508 | '1 ' | 1 | 3 | 12 | 0 | 0 | 128.991 | 0 | 0 | -41.365 | 1 | 1 | 0 | 0 | 0 | 0
6509 | '1 ' | 1 | 3 | 12 | 0 | 0 | 8.495 | 0 | 0 | -2.753 | 1 | 1 | 0 | 0 | 0 | 0
6510 | '1 ' | 1 | 3 | 12 | 0 | 0 | 1971.92 | 0 | 0 | 111.89 | 1 | 1 | 0 | 0 | 0 | 0
7001 | '1 ' | 1 | 3 | 5 | 0 | 0 | 6863.645 | 0 | 0 | -742.359 | 1 | 1 | 0 | 0 | 0 | 0
7002 | '1 ' | 1 | 3 | 5 | 0 | 0 | 2517.078 | 0 | 0 | 134.018 | 1 | 1 | 0 | 0 | 0 | 0
8003 | '1 ' | 1 | 2 | 2 | 0 | 0 | 546.423 | 0 | 0 | -66.307 | 1 | 1 | 0 | 0 | 0 | 0
8004 | '1 ' | 1 | 2 | 2 | 0 | 0 | 3409.103 | 0 | 0 | -444.699 | 1 | 1 | 0 | 0 | 0 | 0
8005 | '1 ' | 1 | 2 | 2 | 0 | 0 | 1213.222 | 0 | 0 | -161.487 | 1 | 1 | 0 | 0 | 0 | 0
0 / END OF LOAD DATA | BEGIN FIXED SHUNT DATA
@! I | 'ID' | STATUS | GL | BL
0 / END OF FIXED SHUNT DATA | BEGIN GENERATOR DATA
@! I | 'ID' | PG | QG | QT | QB | VS | IREG | MBASE | ZR | ZX | RT | XT | GTAP | STAT | RMPCT | PT | PB | O1 | F1 | O2 | F2 | O3 | F3 | O4 | F4 | WMOD | WPF | NREG | Fuel Type |  | Number of Bus |  | Fuel Type | ID
1032 | 'C ' | 712 | -3.332 | 200 | -200 | 1.014 | 1002 | 873 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 873 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1032 |  | UN (Unknown) | C
1032 | 'G ' | 856 | -3.332 | 357 | -357 | 1.014 | 1002 | 1050 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1050 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1032 |  | UN (Unknown) | G
1032 | 'S ' | 520 | -3.332 | 360 | -360 | 1.014 | 1002 | 638 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 638 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 1032 |  | WND (Wind) | S
1034 | 'C ' | 1847 | 262.628 | 500 | -500 | 1.03 | 1004 | 2100 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1944 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1034 |  | UN (Unknown) | C
1034 | 'G ' | 2565 | 262.628 | 918 | -918 | 1.03 | 1004 | 2900 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2700 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1034 |  | UN (Unknown) | G
1034 | 'W ' | 1598 | 262.628 | 800 | -800 | 1.03 | 1004 | 1682 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1682 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 1034 |  | WND (Wind) | W
1131 | 'C ' | 530 | -46.791 | 308 | -308 | 1.01 | 1101 | 1268 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1268 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1131 |  | UN (Unknown) | C
1131 | 'G ' | 2064 | -46.791 | 1916 | -1916 | 1.01 | 1101 | 4934 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4934 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1131 |  | UN (Unknown) | G
1232 | 'C ' | 2728 | 0.604 | 1208 | -1208 | 1.08 | 1202 | 4977 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4977 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1232 |  | UN (Unknown) | C
1232 | 'H ' | 657 | 0.604 | 628 | -628 | 1.08 | 1202 | 1199 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1199 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1232 |  | UN (Unknown) | H
1331 | 'G ' | 1986 | 24.69 | 841 | -841 | 1.045 | 1301 | 2167 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2167 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1331 |  | UN (Unknown) | G
1331 | 'H ' | 2133 | 24.69 | 1219 | -1219 | 1.045 | 1301 | 2328 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2328 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1331 |  | UN (Unknown) | H
1333 | 'C ' | 218 | 217.32 | 303 | -303 | 1.005 | 1303 | 418 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 418 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1333 |  | UN (Unknown) | C
1333 | 'G ' | 3662 | 217.32 | 2746 | -2746 | 1.005 | 1303 | 7011 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 7011 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1333 |  | UN (Unknown) | G
1333 | 'S ' | 1266 | 217.32 | 1300 | -1300 | 1.005 | 1303 | 2423 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2423 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 1333 |  | WND (Wind) | S
1431 | 'G ' | 5129 | 409.166 | 3559 | -3559 | 1.035 | 1401 | 9170 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 9170 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 1431 |  | UN (Unknown) | G
1431 | 'N ' | 2355 | 409.166 | 2057 | -2057 | 1.035 | 1401 | 4210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4210 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 1431 |  | WND (Wind) | N
1431 | 'S ' | 1353 | 409.166 | 1000 | -1000 | 1.035 | 1401 | 2419 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2419 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 1431 |  | UN (Unknown) | S
2030 | 'E ' | 605 | 142.477 | 350 | -350 | 1 | 2000 | 699 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 699 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2030 |  | UN (Unknown) | E
2030 | 'G ' | 1853 | 142.477 | 1070 | -1070 | 1 | 2000 | 2140 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2140 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2030 |  | UN (Unknown) | G
2130 | 'E ' | 573 | 28.722 | 254 | -254 | 1.035 | 2100 | 831 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 831 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2130 |  | UN (Unknown) | E
2130 | 'G ' | 404 | 28.722 | 200 | -200 | 1.035 | 2100 | 586 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 586 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 2130 |  | WND (Wind) | G
2130 | 'H ' | 273 | 28.722 | 250 | -250 | 1.035 | 2100 | 396 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 396 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2130 |  | UN (Unknown) | H
2130 | 'S ' | 79 | 28.722 | 86 | -86 | 1.035 | 2100 | 115 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 115 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 2130 |  | UN (Unknown) | S
2233 | 'DG' | 285 | 125.466 | 304 | -118 | 1.005 | 2203 | 1035 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1035 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2233 |  | UN (Unknown) | DG
2233 | 'EG' | 506 | 125.466 | 611 | -181 | 1.005 | 2203 | 1837 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1837 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2233 |  | UN (Unknown) | EG
2233 | 'TG' | 202 | 125.466 | 206 | -155 | 1.005 | 2203 | 733 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 733 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2233 |  | UN (Unknown) | TG
2332 | 'S ' | 878 | 42.001 | 590 | -364 | 1.035 | 2302 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2332 |  | WND (Wind) | S
2431 | 'S ' | 500 | -46.886 | 800 | -800 | 1.05 | 2431 | 1666 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1666 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2431 |  | WND (Wind) | S
2434 | 'S ' | 500 | -337.252 | 500 | -500 | 1.02 | 2434 | 1489 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1489 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2434 |  | WND (Wind) | S
2438 | 'EG' | 503 | 32.102 | 728 | -454 | 1.009 | 2408 | 2292 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2292 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2438 |  | UN (Unknown) | EG
2438 | 'ND' | 0 | 0 | 0.5 | 0 | 1.009 | 2408 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -1006 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2438 |  | UN (Unknown) | ND
2438 | 'RG' | 1195.999 | 32.102 | 1902 | -1168 | 1.009 | 2408 | 5451 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5451 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 2438 |  | WND (Wind) | RG
2438 | 'S ' | 251 | 32.102 | 800 | -800 | 1.009 | 2408 | 1146 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1146 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 2438 |  | UN (Unknown) | S
2438 | 'SG' | 901 | 32.102 | 2301 | -1053 | 1.009 | 2408 | 4110 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4110 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2438 |  | UN (Unknown) | SG
2438 | 'SH' | 233 | 32.102 | 659 | -523 | 1.009 | 2408 | 1460 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1460 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2438 |  | UN (Unknown) | SH
2438 | 'SW' | 704 | 32.102 | 561 | -553 | 1.009 | 2408 | 3210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3210 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2438 |  | WND (Wind) | SW
2438 | 'WG' | 1276 | 32.102 | 1910 | -1150 | 1.009 | 2408 | 5817 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5817 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2438 |  | UN (Unknown) | WG
2439 | 'S ' | 1000 | -242.186 | 800 | -800 | 1.02 | 2409 | 1666 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1666 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2439 |  | WND (Wind) | S
2533 | 'S ' | 1899 | 127.613 | 1100 | -820 | 1.009 | 2503 | 1999 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1999 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2533 |  | WND (Wind) | S
2630 | 'G ' | 2282 | 184.814 | 1346 | -1346 | 1.004 | 2610 | 3947 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3947 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2630 |  | UN (Unknown) | G
2631 | 'S ' | 232 | 32.063 | 350 | -350 | 1.015 | 2611 | 520 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 520 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 2631 |  | WND (Wind) | S
2634 | 'C ' | 1537 | -18.88 | 950 | -950 | 1.03 | 2604 | 1900 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1618 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2634 |  | UN (Unknown) | C
2637 | 'H ' | 83 | 40.647 | 110 | -110 | 1.0136 | 2612 | 200 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 87 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2637 |  | UN (Unknown) | H
2638 | 'H ' | 200 | 7.74 | 100 | -100 | 1.015 | 2608 | 407 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 407 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 2638 |  | UN (Unknown) | H
3133 | 'NG' | 31 | -12.551 | 42 | -29 | 0.99272 | 3103 | 80 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 62 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3133 |  | UN (Unknown) | NG
3133 | 'SC' | 0 | 0 | 500 | -500 | 0.99272 | 3103 | 300 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0.1 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3133 |  | UN (Unknown) | SC
3135 | 'MG' | 206 | 42.757 | 239 | -201 | 1 | 3105 | 541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 541 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3135 |  | UN (Unknown) | MG
3135 | 'NG' | 14 | 42.757 | 100 | -85 | 1 | 3105 | 38 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 38 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3135 |  | UN (Unknown) | NG
3234 | 'DG' | 104 | 101 | 101 | -75 | 1.01 | 3204 | 177 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 177 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3234 |  | UN (Unknown) | DG
3234 | 'MG' | 2261 | 118.878 | 1244 | -1234 | 1.01 | 3204 | 3853 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3853 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3234 |  | UN (Unknown) | MG
3234 | 'NG' | 608 | 118.878 | 382 | -212 | 1.01 | 3204 | 1037 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1037 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3234 |  | UN (Unknown) | NG
3234 | 'NW' | 1021 | 118.878 | 150 | -110 | 1.01 | 3204 | 1740 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1740 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 3234 |  | WND (Wind) | NW
3333 | 'CG' | 620 | 81.668 | 398 | -226 | 1 | 3303 | 1012 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1012 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3333 |  | UN (Unknown) | CG
3333 | 'NG' | 191 | 81.668 | 202 | -143 | 1 | 3303 | 312 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 312 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3333 |  | UN (Unknown) | NG
3432 | 'NP' | 0 | 0 | 1568 | -941 | 1 | 3402 | 3746 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 3746 | -2841 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3432 |  | UN (Unknown) | NP
3433 | 'NG' | 481 | 25.641 | 231 | -175 | 1 | 3403 | 921 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 921 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3433 |  | UN (Unknown) | NG
3433 | 'S ' | 745 | 25.641 | 939 | -562 | 1 | 3403 | 1426 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1426 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 3433 |  | WND (Wind) | S
3531 | 'CE' | 783 | 30.853 | 1004 | -599 | 1 | 3501 | 1424 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1424 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3531 |  | UN (Unknown) | CE
3531 | 'NE' | 293 | 30.853 | 253 | -181 | 1 | 3501 | 533 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 533 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3531 |  | UN (Unknown) | NE
3531 | 'NH' | 13 | 13 | 13 | -10 | 1 | 3501 | 24 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 24 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3531 |  | UN (Unknown) | NH
3631 | 'NB' | 30 | -14 | 20 | -14 | 1.015 | 3601 | 96 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 96 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3631 |  | UN (Unknown) | NB
3631 | 'NG' | 67 | -33.095 | 74 | -34 | 1.015 | 3601 | 210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 210 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3631 |  | UN (Unknown) | NG
3731 | 'NH' | 222 | -121 | 200 | -121 | 1 | 3701 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 243 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3731 |  | UN (Unknown) | NH
3831 | 'NN' | 2108 | -40.709 | 1175 | -980 | 1.049 | 3801 | 2323 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2323 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3831 |  | UN (Unknown) | NN
3835 | 'ND' | 0 | 0 | 0.5 | 0 | 1.035 | 3805 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -510 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3835 |  | UN (Unknown) | ND
3835 | 'NG' | 229 | 28.865 | 662 | -479 | 1.035 | 3805 | 2025 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2025 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 3835 |  | WND (Wind) | NG
3835 | 'S ' | 150 | 28.865 | 500 | -500 | 1.035 | 3805 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 3835 |  | UN (Unknown) | S
3836 | 'DG' | 679 | -6.822 | 476 | -352 | 1.019 | 3806 | 1497 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1497 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3836 |  | UN (Unknown) | DG
3931 | 'NB' | 235 | 72.471 | 151 | -115 | 1.07 | 3921 | 567 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 567 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3931 |  | UN (Unknown) | NB
3931 | 'NH' | 1212 | 72.471 | 1284 | -946 | 1.07 | 3921 | 2875 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2875 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3931 |  | UN (Unknown) | NH
3932 | 'S ' | 1355 | -242.757 | 1150 | -500 | 1 | 3902 | 1426 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1426 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 3932 |  | WND (Wind) | S
3933 | 'CG' | 404.88 | 88.652 | 363 | -82 | 1.02 | 3933 | 865 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 865 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 3933 |  | WND (Wind) | CG
3933 | 'NB' | 161.484 | 77 | 77 | -55 | 1.02 | 3933 | 345 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 345 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 3933 |  | WND (Wind) | NB
3933 | 'ND' | 0 | 0 | 0.5 | 0 | 1.02 | 3933 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -449 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3933 |  | UN (Unknown) | ND
3933 | 'NG' | 901.97 | 88.652 | 500 | -307 | 1.02 | 3933 | 1927 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1927 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3933 |  | UN (Unknown) | NG
3933 | 'NH' | 1275.022 | 88.652 | 1256 | -1041 | 1.02 | 3933 | 2774 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2724 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 3933 |  | UN (Unknown) | NH
3933 | 'NW' | 346.372 | 88.652 | 200 | -200 | 1.02 | 3933 | 740 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 740 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 3933 |  | UN (Unknown) | NW
3933 | 'S ' | 623.937 | 88.652 | 800 | -500 | 1.02 | 3933 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 3933 |  | UN (Unknown) | S
4031 | 'G ' | 892.801 | -168.528 | 502 | -502 | 1.08 | 4001 | 2710 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2710 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4031 |  | UN (Unknown) | G
4031 | 'H ' | 313.199 | -168.528 | 489 | -489 | 1.08 | 4001 | 952 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 952 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 4031 |  | WND (Wind) | H
4031 | 'S ' | 140.4 | -168.528 | 250 | -250 | 1.08 | 4001 | 427 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 427 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 4031 |  | WND (Wind) | S
4031 | 'W ' | 208.8 | -168.528 | 240 | -240 | 1.08 | 4001 | 635 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 635 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 4031 |  | UN (Unknown) | W
4035 | 'C ' | 173.7 | -122.614 | 255 | -255 | 1.08 | 4005 | 642 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 642 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 4035 |  | WND (Wind) | C
4035 | 'G ' | 448.2 | -122.614 | 307 | -307 | 1.08 | 4005 | 1656 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1656 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4035 |  | UN (Unknown) | G
4035 | 'H ' | 966.6 | -122.614 | 1836 | -1836 | 1.08 | 4005 | 3572 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3572 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4035 |  | UN (Unknown) | H
4035 | 'W ' | 697.5 | -122.614 | 800 | -800 | 1.08 | 4005 | 2578 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2578 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 4035 |  | UN (Unknown) | W
4039 | 'G ' | 77.4 | 102 | 102 | -102 | 1.08 | 4009 | 150 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 150 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4039 |  | UN (Unknown) | G
4039 | 'H ' | 1455.3 | 380.224 | 1459 | -1459 | 1.08 | 4009 | 2839 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2839 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4039 |  | UN (Unknown) | H
4039 | 'W ' | 712.8 | 380.224 | 500 | -500 | 1.08 | 4009 | 1290 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1290 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 4039 |  | WND (Wind) | W
4131 | 'B ' | 450 | 150 | 150 | -150 | 1.128 | 4101 | 711 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 711 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4131 |  | UN (Unknown) | B
4131 | 'H ' | 7418.7 | 543.401 | 6482 | -6482 | 1.128 | 4101 | 12613 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 12613 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4131 |  | UN (Unknown) | H
4131 | 'W ' | 555.3 | 120 | 120 | -120 | 1.128 | 4101 | 790 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 790 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 4131 |  | WND (Wind) | W
4132 | 'G ' | 1854.899 | 52.261 | 1473 | -1473 | 1.096 | 4102 | 2170 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2170 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4132 |  | UN (Unknown) | G
4132 | 'H ' | 3835.801 | 52.261 | 2847 | -2847 | 1.096 | 4102 | 5539 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5539 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4132 |  | UN (Unknown) | H
4132 | 'N ' | 900 | 52.261 | 231 | -231 | 1.096 | 4102 | 1200 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1200 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 4132 |  | WND (Wind) | N
4132 | 'W ' | 270 | 52.261 | 160 | -160 | 1.096 | 4102 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 300 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 4132 |  | UN (Unknown) | W
4231 | 'C ' | 999 | 485.229 | 728 | -728 | 1.12 | 4201 | 1460 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1460 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4231 |  | UN (Unknown) | C
4231 | 'G ' | 664.2 | 485.229 | 659 | -659 | 1.12 | 4201 | 970 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 970 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4231 |  | UN (Unknown) | G
4231 | 'H ' | 2406.601 | 485.229 | 1808 | -1808 | 1.12 | 4201 | 3517 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3517 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4231 |  | UN (Unknown) | H
4232 | 'G ' | 348.3 | -3.607 | 592 | -592 | 1.06 | 4202 | 872 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 872 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 4232 |  | UN (Unknown) | G
4232 | 'H ' | 222.3 | -3.607 | 287 | -287 | 1.06 | 4202 | 558 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 558 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 4232 |  | WND (Wind) | H
4232 | 'W ' | 316.8 | -3.607 | 108 | -108 | 1.06 | 4202 | 695 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 695 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 4232 |  | UN (Unknown) | W
5031 | 'G ' | 821.7 | 534.329 | 605 | -605 | 1.05 | 5001 | 2650 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2650 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 5031 |  | UN (Unknown) | G
5031 | 'H ' | 5976 | 534.329 | 4399 | -4399 | 1.05 | 5001 | 10747 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 10747 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 5031 |  | UN (Unknown) | H
5032 | 'C ' | 3646.8 | 410.28 | 2977 | -2977 | 1.055 | 5002 | 13039 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 13039 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 5032 |  | WND (Wind) | C
5032 | 'G ' | 2695.5 | 410.28 | 2200 | -2200 | 1.055 | 5002 | 9636 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 9636 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 5032 |  | UN (Unknown) | G
5032 | 'R ' | 66.6 | 54 | 54 | -54 | 1.055 | 5002 | 108 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 108 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 5032 |  | UN (Unknown) | R
5032 | 'S ' | 2701.8 | 410.28 | 2205 | -2205 | 1.055 | 5002 | 4410.2 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4410.2 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 5032 |  | UN (Unknown) | S
5032 | 'W ' | 331.2 | 271 | 271 | -271 | 1.055 | 5002 | 541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 541 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 5032 |  | WND (Wind) | W
6132 | 'B ' | 45 | -20 | 20 | -20 | 1.03 | 6102 | 122 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 122 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6132 |  | UN (Unknown) | B
6132 | 'G ' | 1043.1 | -147 | 147 | -147 | 1.03 | 6102 | 1272 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1272 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6132 |  | UN (Unknown) | G
6132 | 'H ' | 1992.599 | -387.445 | 1072 | -1072 | 1.03 | 6102 | 2541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2541 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 6132 |  | WND (Wind) | H
6132 | 'S ' | 180 | -75 | 75 | -75 | 1.03 | 6102 | 395 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 395 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 6132 |  | UN (Unknown) | S
6132 | 'W ' | 503.1 | -210 | 210 | -210 | 1.03 | 6102 | 973 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 973 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 6132 |  | WND (Wind) | W
6231 | 'C ' | 705.15 | -104.087 | 1256 | -1256 | 1.06 | 6201 | 2488 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2488 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6231 |  | UN (Unknown) | C
6231 | 'G ' | 225 | -70 | 70 | -70 | 1.06 | 6201 | 250 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 250 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6231 |  | UN (Unknown) | G
6235 | 'G ' | 90 | 49.769 | 64 | -64 | 1.05 | 6205 | 226 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 226 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6235 |  | UN (Unknown) | G
6235 | 'H ' | 1040.4 | 49.769 | 347 | -347 | 1.05 | 6205 | 2671 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2671 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 6235 |  | WND (Wind) | H
6235 | 'W ' | 280.8 | 49.769 | 195 | -195 | 1.05 | 6205 | 720 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 720 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 6235 |  | UN (Unknown) | W
6333 | 'C ' | 2837.7 | 330.576 | 1671 | -1671 | 1.03 | 6303 | 4594 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4594 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6333 |  | UN (Unknown) | C
6333 | 'W ' | 919.8 | 330.576 | 350 | -350 | 1.03 | 6303 | 1489 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1489 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 6333 |  | WND (Wind) | W
6335 | 'C ' | 2274.3 | 260.575 | 968 | -968 | 1.06 | 6305 | 3000 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2660 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6335 |  | UN (Unknown) | C
6335 | 'G ' | 295.2 | 260.575 | 330 | -330 | 1.06 | 6305 | 418 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 418 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6335 |  | UN (Unknown) | G
6335 | 'H ' | 259.2 | 260.575 | 406 | -406 | 1.06 | 6305 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 303 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6335 |  | UN (Unknown) | H
6433 | 'C ' | 194 | 74.552 | 283 | -283 | 1.11 | 6403 | 391 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 391 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6433 |  | UN (Unknown) | C
6433 | 'E ' | 372 | 59 | 59 | -59 | 1.11 | 6403 | 751 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 751 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6433 |  | UN (Unknown) | E
6433 | 'G ' | 679 | 74.552 | 536 | -536 | 1.11 | 6403 | 1369 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1369 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6433 |  | UN (Unknown) | G
6433 | 'W ' | 75 | 50 | 50 | -50 | 1.11 | 6403 | 152 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 152 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) |  | 6433 |  | WND (Wind) | W
6533 | 'C ' | 1318.501 | 78.734 | 1924 | -1924 | 1.065 | 6503 | 3276 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3276 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 6533 |  | WND (Wind) | C
6533 | 'G ' | 1213.201 | 78.734 | 880 | -880 | 1.065 | 6503 | 3239 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3239 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 6533 |  | WND (Wind) | G
6533 | 'H ' | 90 | 75 | 75 | -75 | 1.065 | 6503 | 275 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 275 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 6533 |  | UN (Unknown) | H
6533 | 'S ' | 566.1 | 78.734 | 500 | -500 | 1.065 | 6503 | 1407 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1407 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 6533 |  | UN (Unknown) | S
6533 | 'W ' | 157.5 | 20 | 20 | -20 | 1.065 | 6503 | 391 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 391 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 6533 |  | UN (Unknown) | W
7031 | 'C ' | 1105.199 | 380.609 | 1419 | -1419 | 1.02 | 7001 | 3127 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3127 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 7031 |  | UN (Unknown) | C
7031 | 'G ' | 2242.802 | 380.609 | 2092 | -2092 | 1.02 | 7001 | 6346 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 6346 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 7031 |  | UN (Unknown) | G
7031 | 'P ' | 123.3 | 175 | 175 | -175 | 1.02 | 7001 | 509 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 509 | -509 | 1 | 1 | [9 empty] | WND (Wind) |  | 7031 |  | WND (Wind) | P
7031 | 'SC' | 0 | 0 | 1000 | -1000 | 1.02 | 7001 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0.1 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 7031 |  | UN (Unknown) | SC
7031 | 'W ' | 1098 | 380.609 | 1000 | -1000 | 1.02 | 7001 | 3106 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3106 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 7031 |  | UN (Unknown) | W
7032 | 'C ' | 1057.5 | 22.012 | 826 | -826 | 1.015 | 7002 | 1821 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1821 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 7032 |  | UN (Unknown) | C
7032 | 'G ' | 861.3 | 22.012 | 489 | -489 | 1.015 | 7002 | 1483 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1483 | 0 | 1 | 1 | [9 empty] | WND (Wind) |  | 7032 |  | WND (Wind) | G
7032 | 'H ' | 390.6 | 22.012 | 346 | -346 | 1.015 | 7002 | 672 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 672 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 7032 |  | UN (Unknown) | H
7032 | 'S ' | 428.4 | 22.012 | 230 | -230 | 1.015 | 7002 | 738 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 738 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) |  | 7032 |  | UN (Unknown) | S
8033 | 'H ' | 1182 | 259.732 | 786 | -786 | 1.075 | 8003 | 1394 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1394 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 8033 |  | UN (Unknown) | H
8034 | 'G ' | 2946 | 239.367 | 1280 | -1280 | 1 | 8004 | 3754 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3754 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 8034 |  | UN (Unknown) | G
8034 | 'H ' | 427 | 239.367 | 344 | -344 | 1 | 8004 | 544 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 544 | 0 | 1 | 1 | [9 empty] | UN (Unknown) |  | 8034 |  | UN (Unknown) | H
0 / END OF GENERATOR DATA | BEGIN BRANCH DATA
@! I | J | 'CKT' | R | X | B | 'N A M E' | RATE1 | RATE2 | RATE3 | RATE4 | RATE5 | RATE6 | RATE7 | RATE8 | RATE9 | RATE10 | RATE11 | RATE12 | GI | BI | GJ | BJ | STAT | MET | LEN | O1 | F1 | O2 | F2 | O3 | F3 | O4 | F4
1001 | 1201 | '1 ' | 0.00177 | 0.03169 | 3.3446 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1001 | 1202 | '9 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1002 | 1004 | '1 ' | 0.0005 | 0.0053 | 0.0882 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1002 | 1102 | '1 ' | 0.00179 | 0.01988 | 2.576 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1002 | 1102 | '2 ' | 0.00179 | 0.01988 | 2.576 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1002 | 6506 | '1 ' | 0.0048 | 0.0436 | 0.7078 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
1004 | 7001 | '1 ' | 0.00811 | 0.1369 | 2.4348 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
1004 | 7002 | '1 ' | 0.00977 | 0.11 | 2 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
1101 | 1401 | '1 ' | 0.0028 | 0.0211 | 1.0194 | ' ' | 0 | 0 | 1630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1101 | 1401 | '2 ' | 0.0028 | 0.0211 | 1.0194 | ' ' | 0 | 0 | 1630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1201 | 1202 | '1 ' | 0.00077 | 0.00536 | 1.3984 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1201 | 1402 | '1 ' | 0.00179 | 0.02592 | 3.3922 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1201 | 2901 | '1 ' | 0.00207 | 0.01369 | 3.9516 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1202 | 1302 | '1 ' | 0.0028 | 0.0211 | 1.0194 | ' ' | 0 | 0 | 1630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1202 | 1402 | '1 ' | 0.00241 | 0.03489 | 4.8656 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1301 | 1302 | '1 ' | 0.0028 | 0.0211 | 1.0194 | ' ' | 0 | 0 | 1630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1301 | 1402 | '1 ' | 0.0028 | 0.0211 | 1.0194 | ' ' | 0 | 0 | 1630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1301 | 1402 | '2 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1301 | 2603 | '1 ' | 0.00179 | 0.02524 | 0.53546 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
1301 | 2901 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1303 | 6507 | '1 ' | 0.00811 | 0.1369 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
1401 | 1402 | '1 ' | 0.0004 | 0.0096 | 0.9038 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1401 | 1402 | '2 ' | 0.0004 | 0.0096 | 0.9038 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1401 | 2301 | '1 ' | 0.00259 | 0.02967 | 2.153 | ' ' | 0 | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1401 | 2400 | '1 ' | 0.00259 | 0.02967 | 2.153 | ' ' | 0 | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
1403 | 2100 | '1 ' | 0.00845 | 0.07034 | 0.15954 | ' ' | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2000 | 2202 | '1 ' | 0.00138 | 0.05399 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2000 | 2302 | '1 ' | 0.00138 | 0.05399 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2100 | 2302 | '1 ' | 0.00845 | 0.07034 | 0.15954 | ' ' | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2201 | 2301 | '1 ' | 0.00179 | 0.02524 | 2.153 | ' ' | 0 | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2202 | 2203 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2202 | 2203 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2202 | 2503 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2203 | 2503 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2203 | 2503 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2400 | 2403 | '1 ' | 0.00042 | 0.00905 | 0.66794 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2402 | '1 ' | 0.00028 | 0.00753 | 0.51736 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2402 | '2 ' | 0.00035 | 0.0075 | 0.5536 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2404 | '1 ' | 0.00044 | 0.01125 | 0.8292 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2404 | '2 ' | 0.00044 | 0.01125 | 0.8292 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2501 | '1 ' | 0.0006 | 0.0128 | 0.9462 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2603 | '1 ' | 0.0002 | 0.0041 | 0.2962 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2401 | 2901 | '1 ' | 0.00193 | 0.02779 | 4.6712 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2401 | 2902 | '1 ' | 0.0019 | 0.031 | 4.1402 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2402 | 2501 | '1 ' | 0.00021 | 0.00457 | 0.32336 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2403 | 2501 | '1 ' | 0.0004 | 0.0093 | 0.6856 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2404 | 3893 | '1 ' | 1e-07 | -0.00935 | 0 | ' ' | 0 | 0 | 2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2404 | 3895 | '1 ' | 1e-07 | -0.00935 | 0 | ' ' | 0 | 0 | 2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2404 | 3897 | '1 ' | 1e-07 | -0.0084 | 0 | ' ' | 0 | 0 | 2100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2405 | 2406 | '1 ' | 0.0014 | 0.0264 | 0.102 | ' ' | 0 | 0 | 3070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2405 | 2410 | '1 ' | 0.00065 | 0.01187 | 0.04672 | ' ' | 0 | 0 | 3070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2405 | 2410 | '2 ' | 0.00065 | 0.01187 | 0.04672 | ' ' | 0 | 0 | 3070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2406 | 2408 | '1 ' | 0.0019 | 0.0258 | 0.0984 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2406 | 2410 | '1 ' | 0.00845 | 0.07034 | 0.15954 | ' ' | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2407 | 2408 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2408 | 2409 | '1 ' | 0.00138 | 0.05399 | 0.15252 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2408 | 2409 | '2 ' | 0.00138 | 0.05399 | 0.15252 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2408 | 2411 | '1 ' | 0.0032 | 0.0395 | 0.144 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2408 | 2502 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2409 | 2502 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2409 | 2503 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2410 | 2411 | '1 ' | 0.00285 | 0.03649 | 0.12656 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2410 | 2411 | '2 ' | 0.00138 | 0.03399 | 0.11252 | ' ' | 0 | 0 | 2320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2502 | 2503 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2502 | 2503 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2600 | 2601 | '1 ' | 0.00074 | 0.01861 | 1.4026 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2600 | 2602 | '1 ' | 0.00082 | 0.01668 | 1.188 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2600 | 2603 | '1 ' | 1e-07 | 0.00159 | 0.12002 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2600 | 2603 | '2 ' | 1e-07 | 0.00159 | 0.12002 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2601 | 2603 | '1 ' | 0.00083 | 0.01884 | 1.6667 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2603 | 2901 | '1 ' | 0.00179 | 0.02524 | 0.53546 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2604 | 6404 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2604 | 6504 | '1 ' | 0.0018 | 0.0245 | 0.4392 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2604 | 6504 | '2 ' | 0.0018 | 0.0245 | 0.4392 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2605 | 2607 | '1 ' | 0.0107 | 0.07905 | 0.3667 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2606 | 2607 | '1 ' | 0.0107 | 0.07905 | 0.3667 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2608 | 2611 | '1 ' | 0.00221 | 0.03346 | 0.07338 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2608 | 2612 | '1 ' | 0.0029 | 0.038 | 0.0824 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2608 | 2618 | '1 ' | 0.00309 | 0.04677 | 0.1008 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2608 | 2619 | '1 ' | 0.00226 | 0.03422 | 0.07506 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2609 | 2615 | '1 ' | 0.00047 | 0.00723 | 0.01624 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2609 | 2617 | '1 ' | 0.00035 | 0.00536 | 0.01204 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2610 | 2613 | '1 ' | 0.0022 | 0.03422 | 0.07716 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2610 | 2613 | '2 ' | 0.00238 | 0.03669 | 0.08284 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2610 | 2616 | '1 ' | 0.00201 | 0.03074 | 0.06886 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2610 | 2617 | '1 ' | 0.00281 | 0.04296 | 0.09648 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2611 | 2612 | '1 ' | 0.00029 | 0.00434 | 0.0095 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2612 | 2615 | '1 ' | 0.00229 | 0.01583 | 0.0306 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2615 | '2 ' | 0.00229 | 0.01583 | 0.0306 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2618 | '1 ' | 0.00141 | 0.00967 | 0.0194 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2618 | '2 ' | 0.00141 | 0.00967 | 0.0194 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2618 | '3 ' | 0.00161 | 0.00971 | 0.01928 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2618 | '4 ' | 0.00161 | 0.00971 | 0.01928 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2619 | '1 ' | 0.00027 | 0.00393 | 0.00918 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2619 | '2 ' | 0.00027 | 0.00393 | 0.00918 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2619 | '3 ' | 0.00027 | 0.00393 | 0.00918 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2620 | '1 ' | 0.00138 | 0.01116 | 0.0247 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2612 | 2620 | '2 ' | 0.00138 | 0.01116 | 0.0247 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2613 | 2616 | '1 ' | 0.00037 | 0.00366 | 0.0083 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2613 | 2617 | '1 ' | 0.00055 | 0.00586 | 0.01246 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2614 | 2616 | '1 ' | 0.00073 | 0.01025 | 0.02558 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2614 | 2616 | '2 ' | 0.00073 | 0.01025 | 0.02558 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2615 | 2617 | '1 ' | 0.00119 | 0.01244 | 0.02798 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2615 | 2617 | '2 ' | 0.00119 | 0.01244 | 0.02798 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2615 | 2620 | '1 ' | 0.00128 | 0.00979 | 0.0212 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
2616 | 2617 | '1 ' | 0.0011 | 0.01189 | 0.02514 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
2901 | 2902 | '1 ' | 0.00056 | 0.01415 | 1.0429 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3101 | 3102 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3101 | 3102 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3102 | 3103 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3102 | 3103 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3102 | 3103 | '3 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3102 | 3302 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3103 | 3204 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3103 | 3204 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3103 | 3305 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3103 | 3305 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3104 | 3105 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3202 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3202 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3203 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3203 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3923 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3924 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3201 | 3924 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3202 | 3203 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1
3202 | 3203 | '9 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3202 | 3204 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3202 | 3205 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3202 | 3924 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3202 | 3924 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3204 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3303 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3303 | '9 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3305 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3203 | 3923 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3204 | 3205 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3204 | 3205 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3204 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3204 | 3923 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3205 | 3914 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3205 | 3915 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3301 | 3902 | '1 ' | 0.00053 | 0.01297 | 0 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3301 | 3903 | '1 ' | 0.0005 | 0.00881 | 0.59878 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3302 | 3304 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3302 | 3304 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3303 | 3304 | '1 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3303 | 3304 | '2 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3303 | 3304 | '3 ' | 0.0011 | 0.0127 | 0.048 | ' ' | 0 | 1120 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3303 | 3918 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3303 | 3918 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3305 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3401 | 3402 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3401 | 3402 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3401 | 3404 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3401 | 3405 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3401 | 3405 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3401 | 3804 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3403 | 3404 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3403 | 3804 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3404 | 3804 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1
3404 | 3804 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3404 | 3917 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3404 | 3918 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3405 | 3907 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3405 | 3907 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3501 | 3914 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3501 | 3915 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3601 | 3925 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3701 | 3926 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3701 | 3926 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3801 | 3802 | '1 ' | 0.00079 | 0.01937 | 1.3285 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3801 | 3803 | '1 ' | 0.00087 | 0.02087 | 1.4571 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3801 | 3803 | '2 ' | 0.00087 | 0.02087 | 1.4571 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3802 | 3891 | '1 ' | 0.00072 | 0.016 | 1.0879 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3802 | 3901 | '1 ' | 0.00083 | 0.01985 | 0 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3803 | 3891 | '1 ' | 2e-05 | -0.00998 | 0 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3803 | 3892 | '1 ' | 1e-07 | -0.00935 | 0 | ' ' | 0 | 0 | 2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3803 | 3894 | '1 ' | 1e-07 | -0.00944 | 0 | ' ' | 0 | 0 | 2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3803 | 3896 | '1 ' | 1e-07 | -0.00935 | 0 | ' ' | 0 | 0 | 2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3803 | 3901 | '1 ' | 0.00153 | 0.0147 | 0 | ' ' | 0 | 0 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3804 | 3806 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3805 | 3806 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3892 | 3893 | '1 ' | 0.00123 | 0.02659 | 1.987 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3894 | 3895 | '1 ' | 0.00123 | 0.02662 | 1.9888 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3896 | 3897 | '1 ' | 0.00112 | 0.02517 | 1.8359 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3901 | 3902 | '1 ' | 0.00053 | 0.01297 | 0 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3901 | 3903 | '1 ' | 0.00093 | 0.03644 | 1.3895 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3901 | 8002 | '1 ' | 0.00068 | 0.01585 | 1.1513 | ' ' | 0 | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3903 | 3904 | '1 ' | 1e-05 | 0.00359 | 0.97812 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3903 | 3905 | '9 ' | 0.00098 | 0.01035 | 0 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3903 | 8002 | '1 ' | 0.00165 | 0.05719 | 2.4774 | ' ' | 0 | 0 | 2450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3904 | 3905 | '9 ' | 0.0016 | 0.01229 | 0 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3905 | 3906 | '9 ' | 0.00072 | 0.00346 | 0 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3906 | 4001 | '1 ' | 0.00053 | 0.00456 | 0.7635 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3906 | 4001 | '2 ' | 0.00053 | 0.00456 | 0.7635 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3907 | 3908 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3907 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3907 | 8004 | '1 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3908 | 3920 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3909 | 3919 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3909 | 3920 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3910 | 3911 | '1 ' | 0.02482 | 0.16938 | 0.20232 | ' ' | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3910 | 3924 | '1 ' | 0.0148 | 0.10101 | 0.12066 | ' ' | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3912 | '1 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3916 | '1 ' | 0.01668 | 0.11381 | 0.13608 | ' ' | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3921 | '1 ' | 0.01113 | 0.06678 | 0.07286 | ' ' | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3921 | '2 ' | 0.0105 | 0.0654 | 0.0686 | ' ' | 0 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3921 | '3 ' | 0.01105 | 0.06642 | 0.0716 | ' ' | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 3924 | '1 ' | 0.03903 | 0.27403 | 0.31072 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 8003 | '1 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3911 | 8003 | '2 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3912 | 3924 | '1 ' | 0.03058 | 0.2046 | 0.24472 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3913 | 3920 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3913 | 3920 | '2 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3913 | 3923 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3913 | 8004 | '1 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3915 | 3924 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3916 | 3924 | '1 ' | 0.02235 | 0.16106 | 0.18342 | ' ' | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3919 | 3922 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3920 | 3922 | '1 ' | 0.00312 | 0.02886 | 0.15252 | ' ' | 0 | 986 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
3923 | 8005 | '1 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
3923 | 8005 | '2 ' | 0.01382 | 0.09268 | 0.1106 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4001 | 4090 | '1 ' | 0.00072 | 0.01382 | 1.2757 | ' ' | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4001 | 4094 | '1 ' | 0.00078 | 0.01502 | 1.1381 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4001 | 4097 | '1 ' | 0.00074 | 0.01413 | 1.0663 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4001 | 4204 | '1 ' | 0.00078 | 0.00239 | 1.1381 | ' ' | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4001 | 8001 | '1 ' | 0.00106 | 0.01293 | 0 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4002 | 4003 | '1 ' | 0.00122 | 0.02373 | 2.2071 | ' ' | 0 | 0 | 1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4002 | 4090 | '1 ' | 0.00012 | 0.00238 | 0.21926 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4002 | 4091 | '1 ' | 0.0006 | 0.01036 | 1.0146 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4003 | 6101 | '1 ' | 0.00264 | 0.02689 | 5.2907 | ' ' | 0 | 0 | 1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4004 | 4005 | '1 ' | 0.00063 | 0.01412 | 1.0976 | ' ' | 0 | 0 | 3450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4004 | 4005 | '2 ' | 0.00109 | 0.02408 | 1.5554 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4004 | 4005 | '3 ' | 0.00108 | 0.02409 | 1.5535 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4004 | 4091 | '1 ' | 0.00041 | 0.00737 | 0.72694 | ' ' | 0 | 0 | 3450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4004 | 4092 | '1 ' | 0.00066 | 0.01266 | 0.95976 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4004 | 4095 | '1 ' | 0.00066 | 0.01266 | 0.95976 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4005 | 4006 | '1 ' | 0.00023 | 0.00451 | 0.3332 | ' ' | 0 | 0 | 2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4005 | 4006 | '2 ' | 0.0002 | 0.00446 | 0.305 | ' ' | 0 | 0 | 2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4005 | 4102 | '1 ' | 0.0012 | 0.02316 | 1.7152 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4005 | 4102 | '2 ' | 0.0003 | 0.02 | 3.6 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4005 | 4202 | '1 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4005 | 6202 | '1 ' | 0.00196 | 0.03304 | 1.88 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4006 | 4007 | '1 ' | 1e-05 | 0.0003 | 0.01434 | ' ' | 0 | 0 | 3450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4006 | 4007 | '2 ' | 1e-05 | 0.0003 | 0.01844 | ' ' | 0 | 0 | 3450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4006 | 4202 | '1 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4008 | 6401 | '1 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4009 | 4010 | '1 ' | 6e-05 | 0.00131 | 0.00378 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4009 | 4010 | '2 ' | 6e-05 | 0.00116 | 0.00332 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4009 | 4104 | '1 ' | 0.002 | 0.02 | 0.8 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4092 | 4093 | '1 ' | 1e-07 | 0.00165 | 0 | ' ' | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4093 | 4094 | '1 ' | 1e-07 | -0.01263 | 0 | ' ' | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4095 | 4096 | '1 ' | 1e-07 | 0.00165 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4096 | 4097 | '1 ' | 1e-07 | -0.01263 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4101 | 4102 | '1 ' | 0.00113 | 0.02069 | 1.8553 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4101 | 4102 | '2 ' | 0.00113 | 0.02069 | 1.8553 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4101 | 4103 | '1 ' | 0.0007 | 0.074 | 4.87 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4101 | 4103 | '2 ' | 0.002 | 0.02 | 0.8 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4101 | 4201 | '1 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4101 | 4201 | '2 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4102 | 4201 | '1 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4102 | 4201 | '2 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4102 | 4202 | '1 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4102 | 4202 | '2 ' | 0.0002 | 0.0082 | 1.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4102 | 6202 | '1 ' | 0.00142 | 0.02258 | 1.88 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4103 | 6202 | '1 ' | 0.0007 | 0.074 | 4.87 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4104 | 5004 | '1 ' | 0.002 | 0.08 | 0.8 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4201 | 4202 | '1 ' | 0.00109 | 0.02408 | 1.5554 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
4201 | 5001 | '1 ' | 0.00083 | 0.02 | 3.3 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4202 | 4203 | '1 ' | 0.00066 | 0.00165 | 0.95976 | ' ' | 0 | 0 | 3020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
4203 | 4204 | '1 ' | 0.00074 | 0.01266 | 1.0822 | ' ' | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
5001 | 5002 | '1 ' | 0.0035 | 0.007 | 4.606 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
5003 | 5004 | '1 ' | 0.002 | 0.08 | 0.8 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6102 | 6103 | '1 ' | 0.0012 | 0.002316 | 1.7152 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6102 | 6301 | '1 ' | 1e-07 | 0.0046 | 0.3 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6102 | 6403 | '1 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6103 | 6301 | '1 ' | 1e-07 | 0.0046 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6103 | 6301 | '2 ' | 1e-07 | 0.0046 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6103 | 6501 | '1 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6103 | 6501 | '2 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6104 | 6204 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6104 | 6305 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6201 | 6202 | '1 ' | 0.00179 | 0.01405 | 3.68 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6203 | 6205 | '1 ' | 0.0007 | 0.074 | 0.4877 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6203 | 6303 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6203 | 6303 | '2 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6203 | 6304 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6204 | 6205 | '1 ' | 0.0007 | 0.025 | 0.487 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6302 | 7001 | '1 ' | 1e-07 | 0.0046 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6303 | 6304 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6303 | 6305 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6303 | 6305 | '2 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6305 | 6510 | '1 ' | 0.00548 | 0.04825 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6305 | 6510 | '2 ' | 0.0054 | 0.04825 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6401 | 6403 | '1 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6401 | 6403 | '2 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6401 | 6404 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6403 | 6404 | '1 ' | 0.0062 | 0.0673 | 1.1156 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6404 | 6507 | '1 ' | 0.0108 | 0.0965 | 0.3296 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6501 | 6502 | '1 ' | 0.0024 | 0.00332 | 0.5849 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 1
6501 | 6504 | '1 ' | 0.0021 | 0.00238 | 0.3845 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6501 | 6509 | '1 ' | 0.0016 | 0.0226 | 0.381 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6501 | 6509 | '2 ' | 0.0016 | 0.0226 | 0.381 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6503 | '1 ' | 0.0052 | 0.0602 | 1.01 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6503 | '2 ' | 0.0049 | 0.0537 | 0.8843 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6504 | '1 ' | 0.0017 | 0.00225 | 0.3992 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1
6502 | 6504 | '2 ' | 0.0021 | 0.00238 | 0.3845 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6504 | '3 ' | 0.0017 | 0.00225 | 0.3992 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6504 | '4 ' | 0.0021 | 0.00238 | 0.3845 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1
6502 | 6508 | '1 ' | 0.0012 | 0.0172 | 0.2987 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6509 | '1 ' | 0.0008 | 0.00106 | 0.2039 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6502 | 6509 | '2 ' | 0.0008 | 0.00106 | 0.2039 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6503 | 6504 | '1 ' | 0.0032 | 0.0349 | 0.5722 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6503 | 6505 | '1 ' | 0.0096 | 0.0878 | 1.4265 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6503 | 6507 | '1 ' | 0.0034 | 0.0374 | 0.6208 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6503 | 6507 | '2 ' | 0.0034 | 0.0372 | 0.6182 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6503 | 6508 | '1 ' | 0.0034 | 0.0392 | 0.6524 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6504 | 6507 | '1 ' | 0.0038 | 0.034 | 0.5824 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6504 | 6507 | '2 ' | 0.0032 | 0.0349 | 0.5722 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
6504 | 7002 | '1 ' | 0.00811 | 0.1369 | 2.4348 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
7001 | 7002 | '1 ' | 1e-07 | 0.0046 | 0 | ' ' | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
8001 | 8002 | '9 ' | 0.00159 | 0.0111 | 0 | ' ' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
8003 | 8004 | '1 ' | 0.01952 | 0.13702 | 0.15536 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
8003 | 8005 | '1 ' | 0.03903 | 0.27403 | 0.31072 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
8003 | 8005 | '2 ' | 0.03903 | 0.27403 | 0.31072 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
8004 | 8005 | '1 ' | 0.01952 | 0.13702 | 0.15536 | ' ' | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1
0 / END OF BRANCH DATA | BEGIN SYSTEM SWITCHING DEVICE DATA
@! I | J | 'CKT' | X | RATE1 | RATE2 | RATE3 | RATE4 | RATE5 | RATE6 | RATE7 | RATE8 | RATE9 | RATE10 | RATE11 | RATE12 | STAT | NSTAT | MET | STYPE | 'NAME'
0 / END OF SYSTEM SWITCHING DEVICE DATA | BEGIN TRANSFORMER DATA
@! I | J | K | 'CKT' | CW | CZ | CM | MAG1 | MAG2 | NMETR | 'N A M E' | STAT | O1 | F1 | O2 | F2 | O3 | F3 | O4 | F4 | 'VECGRP' | ZCOD
@! R1-2 | X1-2 | SBASE1-2 | R2-3 | RATE1: X2-3; RATE2: SBASE2-3; RATE3: R3-1; RATE4: X3-1; RATE5: SBASE3-1; RATE6: VMSTAR; RATE7: ANSTAR
@!WINDV1 | NOMV1 | ANG1 | RATE1-1 | RATE1-2 | RATE1-3 | RATE1-4 | RATE1-5 | RATE1-6 | RATE1-7 | RATE1-8 | RATE1-9 | RATE1-10 | RATE1-11 | RATE1-12 | COD1 | CONT1 | RMA1 | RMI1 | VMA1 | VMI1 | NTP1 | TAB1 | CR1 | CX1 | CNXA1 | NOD1
@!WINDV2 | NOMV2 | ANG2 | RATE2-1 | RATE2-2 | RATE2-3 | RATE2-4 | RATE2-5 | RATE2-6 | RATE2-7 | RATE2-8 | RATE2-9 | RATE2-10 | RATE2-11 | RATE2-12 | COD2 | CONT2 | RMA2 | RMI2 | VMA2 | VMI2 | NTP2 | TAB2 | CR2 | CX2 | CNXA2 | NOD2
@!WINDV3 | NOMV3 | ANG3 | RATE3-1 | RATE3-2 | RATE3-3 | RATE3-4 | RATE3-5 | RATE3-6 | RATE3-7 | RATE3-8 | RATE3-9 | RATE3-10 | RATE3-11 | RATE3-12 | COD3 | CONT3 | RMA3 | RMI3 | VMA3 | VMI3 | NTP3 | TAB3 | CR3 | CX3 | CNXA3 | NOD3
1001 | 1002 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.011 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
1001 | 1002 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.011 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
1002 | 1003 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00028 | 0.0138 | 100
1 | 345 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
1002 | 1003 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00029 | 0.0139 | 100
1 | 345 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
1002 | 1032 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1004 | 1034 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1101 | 1102 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0146 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
1101 | 1102 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0146 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
1101 | 1131 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1202 | 1232 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1301 | 1331 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1302 | 1303 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0072 | 100
1 | 500 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
1303 | 1333 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1303 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
1401 | 1403 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00028 | 0.0138 | 100
1 | 500 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1401 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
1401 | 1431 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 3066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1401 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2000 | 2030 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2100 | 2130 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2100 | 2400 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00028 | 0.0138 | 100
1 | 230 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 500
2201 | 2202 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2201 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2201 | 2202 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2201 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2203 | 2233 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2203 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2301 | 2302 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2301 | 2302 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2302 | 2332 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2302 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2401 | 2431 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0001 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2401 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2402 | 2409 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2402 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2404 | 2411 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.01149 | 100
1 | 500 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2404 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2404 | 2411 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.01149 | 100
1 | 500 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2404 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2404 | 2411 | 0 | '3 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.01149 | 100
1 | 500 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2404 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2405 | 2619 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.00115 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2405 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2408 | 2438 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2408 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2409 | 2439 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0001 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2409 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2411 | 2434 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0001 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2411 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2501 | 2502 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2501 | 2502 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2501 | 2502 | 0 | '3 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2503 | 2533 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2503 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2601 | 2612 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00026 | 0.01386 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2601 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2602 | 2615 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00013 | 0.01386 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2602 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2602 | 2615 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00013 | 0.01386 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2602 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
2603 | 2607 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0002 | 0.02338 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2603 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 287
2604 | 2634 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2604 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2605 | 2621 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00059 | 0.01491 | 100
1 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2605 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 138
2606 | 2621 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00059 | 0.01491 | 100
1 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2606 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 138
2608 | 2638 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2610 | 2630 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2610 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2611 | 2631 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2611 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2612 | 2637 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2612 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
2614 | 2621 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0133 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2614 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 138
2614 | 2621 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0134 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2614 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 138
3102 | 3104 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3103 | 3133 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3105 | 3135 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3204 | 3234 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3204 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3301 | 3303 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3301 | 3303 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3301 | 3303 | 0 | '3 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3303 | 3333 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3303 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3402 | 3432 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3402 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3403 | 3433 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3501 | 3531 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3601 | 3631 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3701 | 3731 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3701 | 6402 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 115 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3701 | 6402 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 115 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3801 | 3831 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3802 | 3804 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3802 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3803 | 3805 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3803 | 3805 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0002 | 0.0119 | 100
1 | 500 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3805 | 3835 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3806 | 3836 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3806 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3901 | 3917 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3901 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3902 | 3918 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3902 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3902 | 3932 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3902 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3903 | 3923 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3903 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3904 | 3924 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0002 | 0.0125 | 100
1 | 500 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3904 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3905 | 3922 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3905 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3906 | 3921 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0001 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3906 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
3911 | 3925 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3911 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3920 | 3926 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3920 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3920 | 3926 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3920 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
3921 | 3931 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3921 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
3923 | 3933 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3923 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4001 | 4008 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0072 | 100
1 | 500 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
4001 | 4031 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4005 | 4035 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4005 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4006 | 4009 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0002 | 0.01181 | 100
1 | 500 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
4006 | 4009 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
9e-05 | 0.00735 | 100
1 | 500 | 0 | 0 | 0 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
4007 | 4010 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.00221 | 100
1 | 500 | 0 | 0 | 0 | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
4009 | 4039 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4009 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4101 | 4131 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4101 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4102 | 4132 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4102 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4103 | 4104 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.01 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
4201 | 4231 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4201 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
4202 | 4232 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4202 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
5001 | 5031 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
5002 | 5003 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.01 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
5002 | 5032 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6101 | 6102 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0072 | 100
1 | 500 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6101 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
6102 | 6132 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6102 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6103 | 6104 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1.0034 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6104 | 1.1 | 0.9 | 1.1 | 0.95 | 30 | 0 | 0 | 0 | 0 | 0
1 | 230
6201 | 6203 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6201 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
6201 | 6231 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6201 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6202 | 6204 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6202 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
6205 | 6235 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6205 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6301 | 6303 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6301 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
6302 | 6304 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1.0029 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6304 | 1.1 | 0.9 | 1.1 | 0.98 | 36 | 0 | 0 | 0 | 0 | 0
1 | 230
6303 | 6333 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6303 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6305 | 6335 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6305 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6401 | 6402 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 345 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6401 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
6401 | 6402 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.00089 | 0.0299 | 100
1 | 345 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6401 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 115
6403 | 6433 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6403 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6501 | 6510 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
6501 | 6510 | 0 | '2 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0181 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6501 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
6503 | 6533 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6503 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
6505 | 6506 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0195 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6505 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 345
7001 | 7031 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
7002 | 7032 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
8001 | 8003 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0001 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8001 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
8002 | 8005 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
0.0003 | 0.0174 | 100
1 | 500 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8002 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 230
8003 | 8033 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8003 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
8004 | 8034 | 0 | '1 ' | 1 | 1 | 1 | 0 | 0 | 2 | ' ' | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | ' '
1e-07 | 0.0005 | 100
1 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8004 | 1.1 | 0.9 | 1.1 | 0.9 | 989 | 0 | 0 | 0 | 0 | 0
1 | 20
0 / END OF TRANSFORMER DATA | BEGIN AREA DATA
@! I | ISW | PDES | PTOL | RATE1: 'ARNAME'
1 | 0 | 0 | 5 | RATE1: 'SOUTH '
2 | 0 | 0 | 5 | RATE1: 'CALIFORNIA '
3 | 0 | 0 | 5 | RATE1: 'NORTH '
4 | 0 | 0 | 5 | RATE1: 'MEXICO '
0 / END OF AREA DATA | BEGIN TWO-TERMINAL DC DATA
@! 'NAME' | MDC | RDC | SETVL | RATE1: VSCHD; RATE2: VCMOD; RATE3: RCOMP; RATE4: DELTI; RATE5: METER DCVMIN; RATE6: CCCITMX; RATE7: CCCACC
@! IPR | NBR | ANMXR | ANMNR | RCR | XCR | EBASR | TRR | TAPR | TMXR | TMNR | STPR | ICR | IFR | ITR | 'IDR' | XCAPR | NDR
@! IPI | NBI | ANMXI | ANMNI | RCI | XCI | EBASI | TRI | TAPI | TMXI | TMNI | STPI | ICI | IFI | ITI | 'IDI' | XCAPI | NDI
0 / END OF TWO-TERMINAL DC DATA | BEGIN VSC DC LINE DATA
@! 'NAME' | MDC | RDC | O1 | RATE1: F1; RATE2: O2; RATE3: F2; RATE4: O3; RATE5: F3; RATE6: O4; RATE7: F4
@!IBUS | TYPE | MODE | DCSET | ACSET | ALOSS | BLOSS | MINLOSS | SMAX | IMAX | PWF | MAXQ | MINQ | VSREG | RMPCT | NREG
0 / END OF VSC DC LINE DATA | BEGIN IMPEDANCE CORRECTION DATA
@!I | T1 | Re(F1) | Im(F1) | T2 | Re(F2) | Im(F2) | T3 | Re(F3) | Im(F3) | T4 | Re(F4) | Im(F4) | T5 | Re(F5) | Im(F5) | T6 | Re(F6) | Im(F6)
@! T7 | Re(F7) | Im(F7) | T8 | Re(F8) | Im(F8) | T9 | Re(F9) | Im(F9) | T10 | Re(F10) | Im(F10) | T11 | Re(F11) | Im(F11) | T12 | Re(F12) | Im(F12)
@! ...
0 / END OF IMPEDANCE CORRECTION DATA | BEGIN MULTI-TERMINAL DC DATA
@! 'NAME' | NCONV | NDCBS | NDCLN | RATE1: MDC; RATE2: VCONV; RATE3: VCMOD; RATE4: VCONVN
@! IB | N | ANGMX | ANGMN | RC | XC | EBAS | TR | TAP | TPMX | TPMN | TSTP | SETVL | DCPF | MARG | CNVCOD
@!IDC | IB | AREA | ZONE | RATE1: 'DCNAME'; RATE2: IDC2; RATE3: RGRND; RATE4: OWNER
@!IDC | JDC | 'DCCKT' | MET | RATE1: RDC; RATE2: LDC
0 / END OF MULTI-TERMINAL DC DATA | BEGIN MULTI-SECTION LINE DATA
@! I | J | 'ID' | MET | DUM1 | DUM2 | DUM3 | DUM4 | DUM5 | DUM6 | DUM7 | DUM8 | DUM9
0 / END OF MULTI-SECTION LINE DATA | BEGIN ZONE DATA
@! I | 'ZONAME'
1 | 'ALBERTA '
2 | 'CALIFORN '
3 | 'ARIZONA '
4 | 'BRITISH '
5 | 'COLORADO '
6 | 'IDAHO '
7 | 'MEXICO '
8 | 'MONTANA '
9 | 'NEVADA '
10 | 'NEW MEXI '
11 | 'OREGON '
12 | 'UTAH '
13 | 'WASHINGT '
14 | 'WYOMING '
0 / END OF ZONE DATA | BEGIN INTER-AREA TRANSFER DATA
@!ARFROM | ARTO | 'TRID' | PTRAN
0 / END OF INTER-AREA TRANSFER DATA | BEGIN OWNER DATA
@! I | 'OWNAME'
1 | 'OWNER1 '
0 / END OF OWNER DATA | BEGIN FACTS DEVICE DATA
@! 'NAME' | I | J | MODE | PDES | QDES | VSET | SHMX | TRMX | VTMN | VTMX | VSMX | IMX | LINX | RMPCT | OWNER | SET1 | SET2 | VSREF | FCREG | 'MNAME' | NREG
0 / END OF FACTS DEVICE DATA | BEGIN SWITCHED SHUNT DATA
@! I | MODSW | ADJM | ST | VSWHI | VSWLO | SWREG | RMPCT | 'RMIDNT' | BINIT | N1 | B1 | N2 | B2 | N3 | B3 | N4 | B4 | N5 | B5 | N6 | B6 | N7 | B7 | N8 | B8 | NREG
4001 | 1 | 0 | 1 | 1.5 | 0.5 | 4001 | 100 | ' ' | 600 | 5 | 200
4005 | 1 | 0 | 1 | 1.5 | 0.5 | 4005 | 100 | ' ' | 0 | 5 | 200
6104 | 1 | 0 | 1 | 1.5 | 0.5 | 6104 | 100 | ' ' | 400 | 5 | 100
6302 | 1 | 0 | 1 | 1.5 | 0.5 | 6302 | 100 | ' ' | 0 | 5 | 200
6304 | 1 | 0 | 1 | 1.5 | 0.5 | 6304 | 100 | ' ' | 600 | 6 | 100
6401 | 1 | 0 | 1 | 1.5 | 0.5 | 6401 | 100 | ' ' | 600 | 5 | 200
7001 | 1 | 0 | 1 | 1.5 | 0.5 | 7001 | 100 | ' ' | 200 | 5 | 200
0 / END OF SWITCHED SHUNT DATA | BEGIN GNE DATA
@! 'NAME' | 'MODEL' | NTERM | BUS1...BUSNTERM | DUM1: NREAL; DUM2: NINTG; DUM3: NCHAR
@!ST | OWNER | NMETR
@! REAL1...REAL(MIN(10 | NREAL))
@! INTG1...INTG(MIN(10 | NINTG))
@! CHAR1...CHAR(MIN(10 | NCHAR))
0 / END OF GNE DATA | BEGIN INDUCTION MACHINE DATA
@! I | 'ID' | ST | SC | DC | AREA | ZONE | OWNER | TC | BC | MBASE | RATEKV | PC | PSET | H | A | B | D | E | RA | XA | XM | R1 | X1 | R2 | X2 | X3 | E1 | SE1 | E2 | SE2 | IA1 | IA2 | XAMULT
0 / END OF INDUCTION MACHINE DATA | BEGIN SUBSTATION DATA
0 / END OF SUBSTATION DATA
Q

## Sheet4
@! I | 'ID' | PG | QG | QT | QB | VS | IREG | MBASE | ZR | ZX | RT | XT | GTAP | STAT | RMPCT | PT | PB | O1 | F1 | O2 | F2 | O3 | F3 | O4 | F4 | WMOD | WPF | NREG | Fuel Type | Number of Bus | Fuel Type | ID | 873 | 638 | 638 | sum of MBASE for UN | 212961.2
1032 | 'C ' | 712 | -3.332 | 200 | -200 | 1.014 | 1002 | 873 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 873 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1032 | UN (Unknown) | C | 1050 | 1682 | 1682 | sum of MBASE for wind | 70472
1032 | 'G ' | 856 | -3.332 | 357 | -357 | 1.014 | 1002 | 1050 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1050 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1032 | UN (Unknown) | G | 2100 | 2423 | 2423 | sum of MBASE for long recordings | 49441.2
1032 | 'S ' | 520 | -3.332 | 360 | -360 | 1.014 | 1002 | 638 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 638 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 1032 | WND (Wind) | S | 2900 | 4210 | 2419
1034 | 'C ' | 1847 | 262.628 | 500 | -500 | 1.03 | 1004 | 2100 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1944 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1034 | UN (Unknown) | C | 1268 | 586 | 115
1034 | 'G ' | 2565 | 262.628 | 918 | -918 | 1.03 | 1004 | 2900 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2700 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1034 | UN (Unknown) | G | 4934 | 1333 | 1333
1034 | 'W ' | 1598 | 262.628 | 800 | -800 | 1.03 | 1004 | 1682 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1682 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 1034 | WND (Wind) | W | 4977 | 1666 | 1666
1131 | 'C ' | 530 | -46.791 | 308 | -308 | 1.01 | 1101 | 1268 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1268 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1131 | UN (Unknown) | C | 1199 | 1489 | 1489
1131 | 'G ' | 2064 | -46.791 | 1916 | -1916 | 1.01 | 1101 | 4934 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4934 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1131 | UN (Unknown) | G | 2167 | 5451 | 1146
1232 | 'C ' | 2728 | 0.604 | 1208 | -1208 | 1.08 | 1202 | 4977 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4977 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1232 | UN (Unknown) | C | 2328 | 3210 | 3210
1232 | 'H ' | 657 | 0.604 | 628 | -628 | 1.08 | 1202 | 1199 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1199 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1232 | UN (Unknown) | H | 418 | 1666 | 1666
1331 | 'G ' | 1986 | 24.69 | 841 | -841 | 1.045 | 1301 | 2167 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2167 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1331 | UN (Unknown) | G | 7011 | 1999 | 1999
1331 | 'H ' | 2133 | 24.69 | 1219 | -1219 | 1.045 | 1301 | 2328 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2328 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1331 | UN (Unknown) | H | 9170 | 520 | 520
1333 | 'C ' | 218 | 217.32 | 303 | -303 | 1.005 | 1303 | 418 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 418 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1333 | UN (Unknown) | C | 2419 | 1740 | 1740
1333 | 'G ' | 3662 | 217.32 | 2746 | -2746 | 1.005 | 1303 | 7011 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 7011 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1333 | UN (Unknown) | G | 699 | 1426 | 1426
1333 | 'S ' | 1266 | 217.32 | 1300 | -1300 | 1.005 | 1303 | 2423 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2423 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 1333 | WND (Wind) | S | 2140 | 2025 | 1333
1431 | 'G ' | 5129 | 409.166 | 3559 | -3559 | 1.035 | 1401 | 9170 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 9170 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 1431 | UN (Unknown) | G | 831 | 1426 | 1426
1431 | 'N ' | 2355 | 409.166 | 2057 | -2057 | 1.035 | 1401 | 4210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4210 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 1431 | WND (Wind) | N | 396 | 865 | 740
1431 | 'S ' | 1353 | 409.166 | 1000 | -1000 | 1.035 | 1401 | 2419 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2419 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 1431 | UN (Unknown) | S | 115 | 345 | 1333
2030 | 'E ' | 605 | 142.477 | 350 | -350 | 1 | 2000 | 699 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 699 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2030 | UN (Unknown) | E | 1035 | 952 | 427
2030 | 'G ' | 1853 | 142.477 | 1070 | -1070 | 1 | 2000 | 2140 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2140 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2030 | UN (Unknown) | G | 1837 | 427 | 635
2130 | 'E ' | 573 | 28.722 | 254 | -254 | 1.035 | 2100 | 831 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 831 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2130 | UN (Unknown) | E | 733 | 642 | 2578
2130 | 'G ' | 404 | 28.722 | 200 | -200 | 1.035 | 2100 | 586 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 586 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 2130 | WND (Wind) | G | 2292 | 1290 | 1290
2130 | 'H ' | 273 | 28.722 | 250 | -250 | 1.035 | 2100 | 396 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 396 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2130 | UN (Unknown) | H | 100 | 790 | 790
2130 | 'S ' | 79 | 28.722 | 86 | -86 | 1.035 | 2100 | 115 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 115 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 2130 | UN (Unknown) | S | 1146 | 1200 | 400
2233 | 'DG' | 285 | 125.466 | 304 | -118 | 1.005 | 2203 | 1035 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1035 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2233 | UN (Unknown) | DG | 4110 | 558 | 695
2233 | 'EG' | 506 | 125.466 | 611 | -181 | 1.005 | 2203 | 1837 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1837 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2233 | UN (Unknown) | EG | 1460 | 13039 | 4410.2
2233 | 'TG' | 202 | 125.466 | 206 | -155 | 1.005 | 2203 | 733 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 733 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2233 | UN (Unknown) | TG | 5817 | 541 | 541
2332 | 'S ' | 878 | 42.001 | 590 | -364 | 1.035 | 2302 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2332 | WND (Wind) | S | 3947 | 2541 | 395
2431 | 'S ' | 500 | -46.886 | 800 | -800 | 1.05 | 2431 | 1666 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1666 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2431 | WND (Wind) | S | 1900 | 973 | 973
2434 | 'S ' | 500 | -337.252 | 500 | -500 | 1.02 | 2434 | 1489 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1489 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2434 | WND (Wind) | S | 200 | 2671 | 720
2438 | 'EG' | 503 | 32.102 | 728 | -454 | 1.009 | 2408 | 2292 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2292 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2438 | UN (Unknown) | EG | 407 | 1489 | 1489
2438 | 'ND' | 0 | 0 | 0.5 | 0 | 1.009 | 2408 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -1006 | 1 | 1 | [9 empty] | UN (Unknown) | 2438 | UN (Unknown) | ND | 80 | 152 | 152
2438 | 'RG' | 1195.999 | 32.102 | 1902 | -1168 | 1.009 | 2408 | 5451 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5451 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 2438 | WND (Wind) | RG | 300 | 3276 | 1407
2438 | 'S ' | 251 | 32.102 | 800 | -800 | 1.009 | 2408 | 1146 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1146 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 2438 | UN (Unknown) | S | 541 | 3239 | 391
2438 | 'SG' | 901 | 32.102 | 2301 | -1053 | 1.009 | 2408 | 4110 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4110 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2438 | UN (Unknown) | SG | 38 | 509 | 3106
2438 | 'SH' | 233 | 32.102 | 659 | -523 | 1.009 | 2408 | 1460 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1460 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2438 | UN (Unknown) | SH | 177 | 1483 | 738
2438 | 'SW' | 704 | 32.102 | 561 | -553 | 1.009 | 2408 | 3210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3210 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2438 | WND (Wind) | SW | 3853
2438 | 'WG' | 1276 | 32.102 | 1910 | -1150 | 1.009 | 2408 | 5817 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5817 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2438 | UN (Unknown) | WG | 1037
2439 | 'S ' | 1000 | -242.186 | 800 | -800 | 1.02 | 2409 | 1666 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1666 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2439 | WND (Wind) | S | 1012
2533 | 'S ' | 1899 | 127.613 | 1100 | -820 | 1.009 | 2503 | 1999 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1999 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2533 | WND (Wind) | S | 312
2630 | 'G ' | 2282 | 184.814 | 1346 | -1346 | 1.004 | 2610 | 3947 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3947 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2630 | UN (Unknown) | G | 3746
2631 | 'S ' | 232 | 32.063 | 350 | -350 | 1.015 | 2611 | 520 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 520 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 2631 | WND (Wind) | S | 921
2634 | 'C ' | 1537 | -18.88 | 950 | -950 | 1.03 | 2604 | 1900 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1618 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2634 | UN (Unknown) | C | 1424
2637 | 'H ' | 83 | 40.647 | 110 | -110 | 1.0136 | 2612 | 200 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 87 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2637 | UN (Unknown) | H | 533
2638 | 'H ' | 200 | 7.74 | 100 | -100 | 1.015 | 2608 | 407 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 407 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 2638 | UN (Unknown) | H | 24
3133 | 'NG' | 31 | -12.551 | 42 | -29 | 0.99272 | 3103 | 80 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 62 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3133 | UN (Unknown) | NG | 96
3133 | 'SC' | 0 | 0 | 500 | -500 | 0.99272 | 3103 | 300 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0.1 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3133 | UN (Unknown) | SC | 210
3135 | 'MG' | 206 | 42.757 | 239 | -201 | 1 | 3105 | 541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 541 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3135 | UN (Unknown) | MG | 400
3135 | 'NG' | 14 | 42.757 | 100 | -85 | 1 | 3105 | 38 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 38 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3135 | UN (Unknown) | NG | 2323
3234 | 'DG' | 104 | 101 | 101 | -75 | 1.01 | 3204 | 177 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 177 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3234 | UN (Unknown) | DG | 100
3234 | 'MG' | 2261 | 118.878 | 1244 | -1234 | 1.01 | 3204 | 3853 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3853 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3234 | UN (Unknown) | MG | 1333
3234 | 'NG' | 608 | 118.878 | 382 | -212 | 1.01 | 3204 | 1037 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1037 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3234 | UN (Unknown) | NG | 1497
3234 | 'NW' | 1021 | 118.878 | 150 | -110 | 1.01 | 3204 | 1740 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1740 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 3234 | WND (Wind) | NW | 567
3333 | 'CG' | 620 | 81.668 | 398 | -226 | 1 | 3303 | 1012 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1012 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3333 | UN (Unknown) | CG | 2875
3333 | 'NG' | 191 | 81.668 | 202 | -143 | 1 | 3303 | 312 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 312 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3333 | UN (Unknown) | NG | 100
3432 | 'NP' | 0 | 0 | 1568 | -941 | 1 | 3402 | 3746 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 3746 | -2841 | 1 | 1 | [9 empty] | UN (Unknown) | 3432 | UN (Unknown) | NP | 1927
3433 | 'NG' | 481 | 25.641 | 231 | -175 | 1 | 3403 | 921 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 921 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3433 | UN (Unknown) | NG | 2774
3433 | 'S ' | 745 | 25.641 | 939 | -562 | 1 | 3403 | 1426 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1426 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 3433 | WND (Wind) | S | 740
3531 | 'CE' | 783 | 30.853 | 1004 | -599 | 1 | 3501 | 1424 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1424 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3531 | UN (Unknown) | CE | 1333
3531 | 'NE' | 293 | 30.853 | 253 | -181 | 1 | 3501 | 533 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 533 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3531 | UN (Unknown) | NE | 2710
3531 | 'NH' | 13 | 13 | 13 | -10 | 1 | 3501 | 24 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 24 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3531 | UN (Unknown) | NH | 635
3631 | 'NB' | 30 | -14 | 20 | -14 | 1.015 | 3601 | 96 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 96 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3631 | UN (Unknown) | NB | 1656
3631 | 'NG' | 67 | -33.095 | 74 | -34 | 1.015 | 3601 | 210 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 210 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3631 | UN (Unknown) | NG | 3572
3731 | 'NH' | 222 | -121 | 200 | -121 | 1 | 3701 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 243 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3731 | UN (Unknown) | NH | 2578
3831 | 'NN' | 2108 | -40.709 | 1175 | -980 | 1.049 | 3801 | 2323 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2323 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3831 | UN (Unknown) | NN | 150
3835 | 'ND' | 0 | 0 | 0.5 | 0 | 1.035 | 3805 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -510 | 1 | 1 | [9 empty] | UN (Unknown) | 3835 | UN (Unknown) | ND | 2839
3835 | 'NG' | 229 | 28.865 | 662 | -479 | 1.035 | 3805 | 2025 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2025 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 3835 | WND (Wind) | NG | 711
3835 | 'S ' | 150 | 28.865 | 500 | -500 | 1.035 | 3805 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 3835 | UN (Unknown) | S | 12613
3836 | 'DG' | 679 | -6.822 | 476 | -352 | 1.019 | 3806 | 1497 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1497 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3836 | UN (Unknown) | DG | 2170
3931 | 'NB' | 235 | 72.471 | 151 | -115 | 1.07 | 3921 | 567 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 567 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3931 | UN (Unknown) | NB | 5539
3931 | 'NH' | 1212 | 72.471 | 1284 | -946 | 1.07 | 3921 | 2875 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2875 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3931 | UN (Unknown) | NH | 400
3932 | 'S ' | 1355 | -242.757 | 1150 | -500 | 1 | 3902 | 1426 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1426 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 3932 | WND (Wind) | S | 1460
3933 | 'CG' | 404.88 | 88.652 | 363 | -82 | 1.02 | 3933 | 865 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 865 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 3933 | WND (Wind) | CG | 970
3933 | 'NB' | 161.484 | 77 | 77 | -55 | 1.02 | 3933 | 345 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 345 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 3933 | WND (Wind) | NB | 3517
3933 | 'ND' | 0 | 0 | 0.5 | 0 | 1.02 | 3933 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0 | -449 | 1 | 1 | [9 empty] | UN (Unknown) | 3933 | UN (Unknown) | ND | 872
3933 | 'NG' | 901.97 | 88.652 | 500 | -307 | 1.02 | 3933 | 1927 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1927 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3933 | UN (Unknown) | NG | 695
3933 | 'NH' | 1275.022 | 88.652 | 1256 | -1041 | 1.02 | 3933 | 2774 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2724 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 3933 | UN (Unknown) | NH | 2650
3933 | 'NW' | 346.372 | 88.652 | 200 | -200 | 1.02 | 3933 | 740 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 740 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 3933 | UN (Unknown) | NW | 10747
3933 | 'S ' | 623.937 | 88.652 | 800 | -500 | 1.02 | 3933 | 1333 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1333 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 3933 | UN (Unknown) | S | 9636
4031 | 'G ' | 892.801 | -168.528 | 502 | -502 | 1.08 | 4001 | 2710 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2710 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4031 | UN (Unknown) | G | 108
4031 | 'H ' | 313.199 | -168.528 | 489 | -489 | 1.08 | 4001 | 952 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 952 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 4031 | WND (Wind) | H | 4410.2
4031 | 'S ' | 140.4 | -168.528 | 250 | -250 | 1.08 | 4001 | 427 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 427 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 4031 | WND (Wind) | S | 122
4031 | 'W ' | 208.8 | -168.528 | 240 | -240 | 1.08 | 4001 | 635 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 635 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 4031 | UN (Unknown) | W | 1272
4035 | 'C ' | 173.7 | -122.614 | 255 | -255 | 1.08 | 4005 | 642 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 642 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 4035 | WND (Wind) | C | 395
4035 | 'G ' | 448.2 | -122.614 | 307 | -307 | 1.08 | 4005 | 1656 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1656 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4035 | UN (Unknown) | G | 2488
4035 | 'H ' | 966.6 | -122.614 | 1836 | -1836 | 1.08 | 4005 | 3572 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3572 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4035 | UN (Unknown) | H | 250
4035 | 'W ' | 697.5 | -122.614 | 800 | -800 | 1.08 | 4005 | 2578 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2578 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 4035 | UN (Unknown) | W | 226
4039 | 'G ' | 77.4 | 102 | 102 | -102 | 1.08 | 4009 | 150 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 150 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4039 | UN (Unknown) | G | 720
4039 | 'H ' | 1455.3 | 380.224 | 1459 | -1459 | 1.08 | 4009 | 2839 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2839 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4039 | UN (Unknown) | H | 4594
4039 | 'W ' | 712.8 | 380.224 | 500 | -500 | 1.08 | 4009 | 1290 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1290 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 4039 | WND (Wind) | W | 3000
4131 | 'B ' | 450 | 150 | 150 | -150 | 1.128 | 4101 | 711 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 711 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4131 | UN (Unknown) | B | 418
4131 | 'H ' | 7418.7 | 543.401 | 6482 | -6482 | 1.128 | 4101 | 12613 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 12613 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4131 | UN (Unknown) | H | 400
4131 | 'W ' | 555.3 | 120 | 120 | -120 | 1.128 | 4101 | 790 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 790 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 4131 | WND (Wind) | W | 391
4132 | 'G ' | 1854.899 | 52.261 | 1473 | -1473 | 1.096 | 4102 | 2170 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2170 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4132 | UN (Unknown) | G | 751
4132 | 'H ' | 3835.801 | 52.261 | 2847 | -2847 | 1.096 | 4102 | 5539 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 5539 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4132 | UN (Unknown) | H | 1369
4132 | 'N ' | 900 | 52.261 | 231 | -231 | 1.096 | 4102 | 1200 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1200 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 4132 | WND (Wind) | N | 275
4132 | 'W ' | 270 | 52.261 | 160 | -160 | 1.096 | 4102 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 300 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 4132 | UN (Unknown) | W | 1407
4231 | 'C ' | 999 | 485.229 | 728 | -728 | 1.12 | 4201 | 1460 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1460 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4231 | UN (Unknown) | C | 391
4231 | 'G ' | 664.2 | 485.229 | 659 | -659 | 1.12 | 4201 | 970 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 970 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4231 | UN (Unknown) | G | 3127
4231 | 'H ' | 2406.601 | 485.229 | 1808 | -1808 | 1.12 | 4201 | 3517 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3517 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4231 | UN (Unknown) | H | 6346
4232 | 'G ' | 348.3 | -3.607 | 592 | -592 | 1.06 | 4202 | 872 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 872 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 4232 | UN (Unknown) | G | 100
4232 | 'H ' | 222.3 | -3.607 | 287 | -287 | 1.06 | 4202 | 558 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 558 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 4232 | WND (Wind) | H | 3106
4232 | 'W ' | 316.8 | -3.607 | 108 | -108 | 1.06 | 4202 | 695 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 695 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 4232 | UN (Unknown) | W | 1821
5031 | 'G ' | 821.7 | 534.329 | 605 | -605 | 1.05 | 5001 | 2650 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2650 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 5031 | UN (Unknown) | G | 672
5031 | 'H ' | 5976 | 534.329 | 4399 | -4399 | 1.05 | 5001 | 10747 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 10747 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 5031 | UN (Unknown) | H | 738
5032 | 'C ' | 3646.8 | 410.28 | 2977 | -2977 | 1.055 | 5002 | 13039 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 13039 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 5032 | WND (Wind) | C | 1394
5032 | 'G ' | 2695.5 | 410.28 | 2200 | -2200 | 1.055 | 5002 | 9636 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 9636 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 5032 | UN (Unknown) | G | 3754
5032 | 'R ' | 66.6 | 54 | 54 | -54 | 1.055 | 5002 | 108 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 108 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 5032 | UN (Unknown) | R | 544
5032 | 'S ' | 2701.8 | 410.28 | 2205 | -2205 | 1.055 | 5002 | 4410.2 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4410.2 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 5032 | UN (Unknown) | S
5032 | 'W ' | 331.2 | 271 | 271 | -271 | 1.055 | 5002 | 541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 541 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 5032 | WND (Wind) | W
6132 | 'B ' | 45 | -20 | 20 | -20 | 1.03 | 6102 | 122 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 122 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6132 | UN (Unknown) | B
6132 | 'G ' | 1043.1 | -147 | 147 | -147 | 1.03 | 6102 | 1272 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1272 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6132 | UN (Unknown) | G
6132 | 'H ' | 1992.599 | -387.445 | 1072 | -1072 | 1.03 | 6102 | 2541 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2541 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 6132 | WND (Wind) | H
6132 | 'S ' | 180 | -75 | 75 | -75 | 1.03 | 6102 | 395 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 395 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 6132 | UN (Unknown) | S
6132 | 'W ' | 503.1 | -210 | 210 | -210 | 1.03 | 6102 | 973 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 973 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 6132 | WND (Wind) | W
6231 | 'C ' | 705.15 | -104.087 | 1256 | -1256 | 1.06 | 6201 | 2488 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2488 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6231 | UN (Unknown) | C
6231 | 'G ' | 225 | -70 | 70 | -70 | 1.06 | 6201 | 250 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 250 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6231 | UN (Unknown) | G
6235 | 'G ' | 90 | 49.769 | 64 | -64 | 1.05 | 6205 | 226 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 226 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6235 | UN (Unknown) | G
6235 | 'H ' | 1040.4 | 49.769 | 347 | -347 | 1.05 | 6205 | 2671 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2671 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 6235 | WND (Wind) | H
6235 | 'W ' | 280.8 | 49.769 | 195 | -195 | 1.05 | 6205 | 720 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 720 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 6235 | UN (Unknown) | W
6333 | 'C ' | 2837.7 | 330.576 | 1671 | -1671 | 1.03 | 6303 | 4594 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 4594 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6333 | UN (Unknown) | C
6333 | 'W ' | 919.8 | 330.576 | 350 | -350 | 1.03 | 6303 | 1489 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1489 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 6333 | WND (Wind) | W
6335 | 'C ' | 2274.3 | 260.575 | 968 | -968 | 1.06 | 6305 | 3000 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 2660 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6335 | UN (Unknown) | C
6335 | 'G ' | 295.2 | 260.575 | 330 | -330 | 1.06 | 6305 | 418 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 418 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6335 | UN (Unknown) | G
6335 | 'H ' | 259.2 | 260.575 | 406 | -406 | 1.06 | 6305 | 400 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 303 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6335 | UN (Unknown) | H
6433 | 'C ' | 194 | 74.552 | 283 | -283 | 1.11 | 6403 | 391 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 391 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6433 | UN (Unknown) | C
6433 | 'E ' | 372 | 59 | 59 | -59 | 1.11 | 6403 | 751 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 751 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6433 | UN (Unknown) | E
6433 | 'G ' | 679 | 74.552 | 536 | -536 | 1.11 | 6403 | 1369 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1369 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6433 | UN (Unknown) | G
6433 | 'W ' | 75 | 50 | 50 | -50 | 1.11 | 6403 | 152 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 152 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | WND (Wind) | 6433 | WND (Wind) | W
6533 | 'C ' | 1318.501 | 78.734 | 1924 | -1924 | 1.065 | 6503 | 3276 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3276 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 6533 | WND (Wind) | C
6533 | 'G ' | 1213.201 | 78.734 | 880 | -880 | 1.065 | 6503 | 3239 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3239 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 6533 | WND (Wind) | G
6533 | 'H ' | 90 | 75 | 75 | -75 | 1.065 | 6503 | 275 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 275 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 6533 | UN (Unknown) | H
6533 | 'S ' | 566.1 | 78.734 | 500 | -500 | 1.065 | 6503 | 1407 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1407 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 6533 | UN (Unknown) | S
6533 | 'W ' | 157.5 | 20 | 20 | -20 | 1.065 | 6503 | 391 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 391 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 6533 | UN (Unknown) | W
7031 | 'C ' | 1105.199 | 380.609 | 1419 | -1419 | 1.02 | 7001 | 3127 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3127 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 7031 | UN (Unknown) | C
7031 | 'G ' | 2242.802 | 380.609 | 2092 | -2092 | 1.02 | 7001 | 6346 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 6346 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 7031 | UN (Unknown) | G
7031 | 'P ' | 123.3 | 175 | 175 | -175 | 1.02 | 7001 | 509 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 509 | -509 | 1 | 1 | [9 empty] | WND (Wind) | 7031 | WND (Wind) | P
7031 | 'SC' | 0 | 0 | 1000 | -1000 | 1.02 | 7001 | 100 | 0 | 0.2 | 0 | 0 | 1 | 0 | 100 | 0.1 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 7031 | UN (Unknown) | SC
7031 | 'W ' | 1098 | 380.609 | 1000 | -1000 | 1.02 | 7001 | 3106 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3106 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 7031 | UN (Unknown) | W
7032 | 'C ' | 1057.5 | 22.012 | 826 | -826 | 1.015 | 7002 | 1821 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1821 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 7032 | UN (Unknown) | C
7032 | 'G ' | 861.3 | 22.012 | 489 | -489 | 1.015 | 7002 | 1483 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1483 | 0 | 1 | 1 | [9 empty] | WND (Wind) | 7032 | WND (Wind) | G
7032 | 'H ' | 390.6 | 22.012 | 346 | -346 | 1.015 | 7002 | 672 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 672 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 7032 | UN (Unknown) | H
7032 | 'S ' | 428.4 | 22.012 | 230 | -230 | 1.015 | 7002 | 738 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 738 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 |  | UN (Unknown) | 7032 | UN (Unknown) | S
8033 | 'H ' | 1182 | 259.732 | 786 | -786 | 1.075 | 8003 | 1394 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 1394 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 8033 | UN (Unknown) | H
8034 | 'G ' | 2946 | 239.367 | 1280 | -1280 | 1 | 8004 | 3754 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 3754 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 8034 | UN (Unknown) | G
8034 | 'H ' | 427 | 239.367 | 344 | -344 | 1 | 8004 | 544 | 0 | 0.2 | 0 | 0 | 1 | 1 | 100 | 544 | 0 | 1 | 1 | [9 empty] | UN (Unknown) | 8034 | UN (Unknown) | H

## Sheet5
@! I | MBASE | Fuel Type | Fuel Type (Re-assign) | sum of MBASE for wind & solar | 70472
1032 | 638 | WND (Wind) | WND (Wind) | sum of MBASE for solar | 46118
1034 | 1682 | WND (Wind) | WND (Wind) | sum of MBASE for wind | 24354
1333 | 2423 | WND (Wind) | WND (Wind)
1431 | 4210 | WND (Wind) | WND (Wind)
2130 | 586 | WND (Wind) | WND (Wind)
2332 | 1333 | WND (Wind) | WND (Wind)
2431 | 1666 | WND (Wind) | WND (Wind)
2434 | 1489 | WND (Wind) | WND (Wind)
2438 | 5451 | WND (Wind) | WND (Wind)
2438 | 3210 | WND (Wind) | WND (Wind)
2439 | 1666 | WND (Wind) | WND (Wind)
2533 | 1999 | WND (Wind) | SOL (Solar)
2631 | 520 | WND (Wind) | SOL (Solar)
3234 | 1740 | WND (Wind) | SOL (Solar)
3433 | 1426 | WND (Wind) | SOL (Solar)
3835 | 2025 | WND (Wind) | SOL (Solar)
3932 | 1426 | WND (Wind) | SOL (Solar)
3933 | 865 | WND (Wind) | SOL (Solar)
3933 | 345 | WND (Wind) | SOL (Solar)
4031 | 952 | WND (Wind) | SOL (Solar)
4031 | 427 | WND (Wind) | SOL (Solar)
4035 | 642 | WND (Wind) | SOL (Solar)
4039 | 1290 | WND (Wind) | SOL (Solar)
4131 | 790 | WND (Wind) | SOL (Solar)
4132 | 1200 | WND (Wind) | SOL (Solar)
4232 | 558 | WND (Wind) | SOL (Solar)
5032 | 13039 | WND (Wind) | SOL (Solar)
5032 | 541 | WND (Wind) | SOL (Solar)
6132 | 2541 | WND (Wind) | SOL (Solar)
6132 | 973 | WND (Wind) | SOL (Solar)
6235 | 2671 | WND (Wind) | SOL (Solar)
6333 | 1489 | WND (Wind) | SOL (Solar)
6433 | 152 | WND (Wind) | SOL (Solar)
6533 | 3276 | WND (Wind) | SOL (Solar)
6533 | 3239 | WND (Wind) | SOL (Solar)
7031 | 509 | WND (Wind) | SOL (Solar)
7032 | 1483 | WND (Wind) | SOL (Solar)